SPECIFICATION FOR THE

LIFT INSTALLATION

AT

# BUILDING NAME

TOWN

| QUANTITY SURVEYORS | ARCHITECTS |
| --- | --- |
| ## NAME | NAME |
| ## ADDRESS | ## ADDRESS |
| ## ADDRESS | ## ADDRESS |
| ## ADDRESS | ## ADDRESS |
| ## TEL NO | TEL NO |
| ## FAX NO | FAX NO |
| ## CONTACT PERSON: NAME | CONTACT PERSON: NAME |
| ## CELL NO | CELL NO |
|  | ELECTRICAL ENGINEER |
|  | NAME |
|  | ## ADDRESS |
|  | ## ADDRESS |
|  | ## ADDRESS |
|  | TEL NO |
|  | FAX NO |
|  | CONTACT PERSON: NAME |
|  | CELL NO |

### DEPARTMENT OF PUBLIC WORKS

CENTRAL GOVERNMENT OFFICES

VERMEULEN STREET

PRETORIA 0001

PRIVATE BAG X65

PRETORIA 0001

## DATE

#### TABLE OF CONTENTS

|  | ##### PAGES |
| --- | --- |
| Specification for the Lift Installation |  |
| Section 1 – General | 1.1 – 1.6 |
| Section 2 – Equipment Requirements | 2.1 – 2.18 |
| Section 3 – Operational Requirements | 3.1 -.3.9 |
| Section 4 – Detail Lift Requirements | 4.1 – 4.* |
| Section 5 – Schedules of Technical Information | 5.1 – 5.* |
| Section 5 – Schedules of Quantities | 6.1 – 6.* |
| Addition Specification – Operation and Maintenance Manuals | AS.1 – AS.6 |
| Annexure A – Schedule of Imported Materials and Equipment | A1 |

SPECIFICATION FOR THE INSTALLATION OF

# LIFTS, ACCESS GOODS LIFTS ONLY AND ESCALATORS

SECTION 1 - GENERAL

## TABLE OF CONTENTS

| Clause |  | Page |
| --- | --- | --- |
|  | Intent of Specification……………………………………………………………. | 1.1 |
|  | Standards and Codes…………………………………………………………… | 1.1 |
|  | Compliance with Regulations…………………………………………………… | 1.1 |
|  | Scope of Work………………………………………………………………….… | 1.2 |
|  | Co-ordinating …………………………………………………………………….. | 1.2 |
|  | Submittals………………………………………………………………………… | 1.3 |
|  | Tests Certificates and Inspections……………………………………………... | 1.3 |
|  | Application to Department of Labour…………………………………………... | 1.4 |
|  | Operating and Maintenance Manuals…………………………………………. | 1.4 |
|  | Guarantee………………………………………………………………………… | 1.4 |
|  | Materials and Workmanship……………………………………………………. | 1.4 |
|  | Imported Equipment……………………………………………………………... | 1.5 |
|  | Brochures…………………………………………………………………………. | 1.6 |

### SECTION 1 – GENERAL

1.	Intent of Specification

The lift specification is intended to cover the complete installation of the lift plant. The minimum equipment requirements are outlined, but do not cover all the details of design and construction. Such details are recognised as being the exclusive responsibility of the lift contractor. It is hereby acknowledged that neither the Principle Agent nor the Consulting Engineer invented or developed any part of the lift system, but have only made selections of capacities, speed, control systems, materials and finishes, as well as specified performance and installation criteria as may be applicable.

In all cases where a device or part of the equipment is referred to in the singular, it is intended that such reference shall apply to as many devices as are required to complete the installation.

2.	Standards and Codes

All work shall be in accordance with the requirements of the SABS1545-1; SABS1545-2; SABS1545-5; SABS1545-10; SABS1543; “Specifications for Lifts, Escalators and Passenger Conveyors” and shall comply with the Occupational Health and Safety Act 85 of 1993 and current regulations of all other codes applicable to this work.

Equipment and materials shall be new and manufactured in accordance with EN-81 standards and approved by the local authorities having the appropriate jurisdiction.

All equipment shall be provided by the same manufacturer.

3.	Compliance with Regulations

The installation shall be erected and tested in accordance with the following Acts and regulations:

- The latest issue of SABS 0142: “Code of Practice for the Wiring of Premises”,

- The Occupational Health and Safety Act, 1993 (Act 85 of 1993) as amended,

- The Local Government Ordinance 1939 (Ordinance 17 of 1939) as amended and the municipal by-laws and any special requirements of the local supply authority,

- The Fire Brigade services Act 1993 Act 99 of 1987 as amended,

- The National Building Regulations and Building Standards Act 1977 (Act 103 of 1977) as emended,

- The Post Office Act 1958 (Act 44 of 1958) as amended,

- The Electricity Act 1984 (Act 41 of 1984) as amended and

- The Regulations of the local Gas Board where applicable.

4.	Scope of Work

- Work included

Design and provide all labour, materials, equipment and services and perform all operations required for lift work as indicated on drawings or specified herein.

Supply and installation of all fixing materials for installation of equipment in the lift shaft.

Supply and installation of the necessary wiring in conduit from the controlling circuit breaker to the power section of the lift controller.

Supply and install conduit and wiring for the car lighting and socket outlets and the termination and connection thereof in the distribution board.

The lift shaft shall be provided with permanently installed electric lighting, which shall be switched from both the pit and the motor room. The highest and lowest luminaires shall be mounted not more than 500mm from the top of the shaft and from the bottom of the pit respectively, with intermediate luminaires mounted at intervals not exceeding 7000mm. The minimum illumination at 1000mm above the car roof and the lift pit shall be 50lux.

The installation of all electrical equipment shall comply with the requirements of the SABS0142 and a Certificate of Compliance shall be issued therefor.

- Work Executed by Other Trades

#### Structural

Lift shafts, pits and motor rooms complete with all access doors and openings as per drawings.

Concrete slabs with up-stands constructed for the lift machine foundations at the top of each lift shaft.

Waterproofing of lift pit after setting of all pit supporting steels and rail inserts. Pit drains or auto draining pumps as required.

#### Electrical

Provision of  a 3-phase, 4-wire, 50Hz 400/231V permanent power supply to a surface mounted distribution board in each machine room in the position shown on drawings. The distribution board will also be equipped with a separate circuit breaker for the shaft and car lighting as well as a separate circuit breaker with earth leakage protection for the socket outlet in the pit and on top of the lift car.

Machine room shall be equipped with sufficient lighting, ventilation and socket outlets as required by the relevant standards and regulations.

If applicable, the standby power supply will be sized to run a predetermined number of lifts simultaneously.

The normal/standby power indicating circuitry shall include, a delayed normally closed potential free contact at 220 Volts/5 Ampere of the emergency power change over switch gear shall be wired to the lift machine room/s and shall be terminated in a suitable junction box. All wire ways or 25mm minimum conduit required to inter-link the lift motor room for the sequencing of lifts in multi-group installations shall be included under this section.

If required, a suitable pit sump pump will be designed, supplied and installed.

5.	Co-ordinating

Due to the nature of the installation, a fixed sequence of operation is required to properly install the complete lift system. The work shall be closely scheduled in order not to delay the entire project.

The Lift Contractor shall familiarise himself with the requirements of the other trades and shall examine the plans and specifications covering each of these sections.

The lift space requirements shall be carefully checked with other trades to ensure that the equipment can be installed in the proper sequence in the space allotted.

6.	Submittals

#### Layout and Shop Drawings

Layout drawings are required for all lift work, including car enclosure and landing entrance co-ordinating drawings. Drawings shall show top clearance above cross-heads and counterweight frames, machine room layouts with power requirements and heat release data, location of all equipment on tops of cars, overhead beams and elevations, and reactions which will be transmitted to the building structure during normal operation of lifts.

Shop drawings are required for car enclosure, landing entrances and signal fixture work showing construction, finish and fastening details. Furthermore, show drawings shall clearly show the motor room construction detail, shaft construction detail including all the required internal supporting beams, pit dividing walls for multi-lift shafts and pit sump pump drains. Composite shop drawings shall be submitted for areas, which require close co-ordination with the work of the different trades.

All special equipment and fixture faceplates shall be submitted for approval. Drawings and samples or brochures shall be submitted for each type of fixture and shall be co-ordinated with the architectural drawings. Final design and material proposed for fixture faceplates and special equipment shall be approved by the Representative/Agent.

##### Samples

All exposed materials and finishes shall be submitted to Representative/Agent for approval in sample form.

The Lift Contractor shall furnish such samples as may be called for and Representative/Agent may reject all materials or workmanship not corresponding with the samples. All approved samples shall be held in safe-keeping until such time as the work to which they apply has been completed.

7.	Tests Certificates and Inspections

The Lift Contractor shall  carry out all the tests and checks required in terms of the document SABS1545-10 Annex A and/or B and issue the necessary Certificate of Compliance prior to final completion

Upon completion of the installation of all equipment and once being in full operation the Lift Contractor shall completely test the lift equipment to demonstrate that the equipment is provided in compliance with the specification. The total costs for these test shall be included in the tendered amount.

The Lift Contractor shall make arrangements for such tests and shall give at least 72 hours written notice to the Representative/Agent, before commencing the test.

In the event of the plant, equipment or installation not passing the test, the Representative/Agent shall be at liberty to deduct from the Contract amount all reasonable expenses incurred by the Employer and/or the Representative/Agent attending the test.

Whenever any installation or equipment is operated for testing or adjusting as provided for above, the Contractor shall operate the entire system for as long a period as may be required to prove satisfactory performance at all times in the occupied space served by that system until the system is handed over.

The Contractor shall provide all labour and supervision required for such operation and the Department may assign operating personnel as observers, but such observation time shall not be counted as instruction time.

After completing the installation or system, all equipment shall be tested, adjusted and readjusted until they operate to the satisfaction and approval of the Representative/ Agent.

The Contractor shall submit certificates of tests carried out to prove the efficiency of all equipment, as well as certificates to be obtained from all relevant authorities, statutory bodies, etc.

8.	Application to Department of Labour

The Lift Contractor shall submit all the necessary drawings and information to the Regional Director of the Department of Labour and shall submit the necessary application for the erection and use of the lifts, access goods lifts only and escalators.

9.	Operating and Maintenance Manuals

The Contractor shall be responsible for the compilation of a complete set of Operating and Maintenance manuals.

This shall be done in accordance with the Additional Specification – Operating and Maintenance manuals.

All information shall be recorded and reproduced in electronic format as well as supplying the Representative/Agent with three sets of hard copies.

Approval of the final Operating and Maintenance Manuals shall be a prerequisite for issuing of a Certificate of Practical Completion of the installation.

10.	Guarantee

After first delivery of the installation, there will follow a 12-month free maintenance period.

During this period the lift contractor shall maintain the lift installation as per the requirements of the Occupational Health and Safety Act. This maintenance shall include systematic examinations, adjustments and lubrication of all lift equipment. Electrical and mechanical parts shall be repaired or replaced whenever it is required to maintain optimum performance without additional cost to the Department, unless the condition was caused by misuse or vandalism of the lift equipment or due to acts of God.

The work under this section shall be performed by competent, qualified personnel under the supervision and in the direct employment of the Lift Contractor and shall not be transferred to any non-affiliated agent. Contract maintenance and repair work shall be done during normal working hours and shall further provide emergency call-back service twenty-four (24) hours a day, seven (7) days a week.

During the guarantee period the Department  will invite tenders for the comprehensive maintenance of the lift installation, which will commence after the final delivery has taken place, i.e. after the twelfth month guarantee period is over and all defects are corrected.

11.	Materials and Workmanship

- The work throughout shall be executed to the highest standards and to the entire satisfaction of the Representative/Agent who shall interpret the meaning of the Contract Document and shall have the authority to reject any work and materials, which, in his judgement, are not in full accordance therewith. All condemned material and workmanship shall be replaced or rectified as directed and approved by the Representative/Agent.

- All work shall be executed in a first-class manner by qualified tradesman.

- The Contractor shall be fully responsible for his work and shall replace any of the work which may be damaged, lost or stolen.  The Contractor shall protect the building and its contents against damage by him, his employees or sub-contractors and shall make good any damage thereto.

- The Contractor shall indemnify the Employer of all liability for damages arising from injuries or disabilities to persons or damage to property occasioned by any act or omission of the Contractor or any of his sub-contractors, including any and all expenses, legal or otherwise, which may be incurred by the Employer or Representative/Agent in the defence of any claim, action or suit.

- The Contractor shall warrant that the materials and workmanship shall be of the highest grade, that the equipment shall be installed in a practical and first-class manner in accordance with the best practices and ready and complete for full operation.  It is specifically intended that all material or labour which is usually provided as part of such equipment as is called for and which is necessary for its proper completion and operation shall be provided without additional cost whether or not shown or described in the Contract Document.

- The Contractor shall thoroughly acquaint himself with the work involved and shall verify on site all measurements necessary for proper installation work. The Contractor shall also be prepared to promptly furnish any information relating to his own work as may be necessary for the proper installation work and shall co-operate with and co-ordinate the work of others as may be applicable.

- The Contractor shall inspect and verify that the existing power feeder system is compatible with the equipment offered and any changes or upgrading of the electrical supply shall be brought to the attention of the Representative/Agent.

- Material and equipment damaged in transit shall be replaced with undamaged material.

- All components and their respective adjustment, which do not form part of the equipment installation work, but influence the optimum and safe operation of the equipment shall be considered to form part of, and shall be included in the Contractor’s scope of works.

- All control equipment and serviceable items shall be installed and positioned such that they will be accessible and maintainable.

- The Contractor shall make sure that all safety regulations and measures are applied and enforced during the installation and guarantee periods to ensure the safety of the public and the User Client.

- The Contractor is to include for all scaffolding required to complete the work required.

12.	Imported Equipment

This equipment will not be subject to fluctuations in the rate of exchange.

However, should the Contractor choose to be protected against fluctuations in the rate of exchange on imported equipment, the following conditions will apply:

a)	The Materials Offered Ex-Import (Annexure A), which forms part of this tender document, must be completed by the Contractor.

b)	Any fluctuations in the rate of exchange will be for the account of the Government and shall be calculated from a date seven (7) days prior to the date of the Contractor's tender to a date seven (7) days after receipt by the Contractor's bank of the negotiable bill of lading or the exporter's invoice, provided this latter date is not later than 30 days after the date of payment. Thereafter, fluctuations in the rate of exchange shall not be for the account of the Government.

13.	Brochures

Detailed brochures of all equipment offered, including the control, drive, door operator, call buttons and signals, remote monitoring station, intercoms and emergency dial-out system shall be presented together with the tender documents.

SPECIFICATION FOR THE INSTALLATION OF

# LIFTS, ACCESS GOODS LIFTS ONLY AND ESCALATORS

SECTION 2 – EQUIPMENT REQUIREMENT

## TABLE OF CONTENTS

| Clause |  | Page |
| --- | --- | --- |
|  | Hoisting Machine………………………………………………………………… | 2.1 |
|  | Controller…………………………………………………………………………. | 2.2 |
|  | Control System…………………………………………………………………... | 2.2 |
|  | Machine Room Indicators……………….………………………………………. | 2.3 |
|  | Safety Gear and Governor …………….……………………………………….. | 2.3 |
|  | Rope Guards………………..………….………………………………………… | 2.4 |
|  | Motor Room Ventilation and Lighting.…………………………………………. | 2.4 |
|  | Machine Data Submittals……………………………………………………….. | 2.4 |
|  | Lift Shaft Requirements…………………………………………………………. | 2.4 |
|  | Car and Counterweight Guide Rails…………………………………………… | 2.4 |
|  | Hoist and Governor Ropes……………………………………………………… | 2.5 |
|  | Counterweight……………………………………………………………………. | 2.5 |
|  | Car and Counterweight Guide Rollers or Shoes……………………………… | 2.5 |
|  | Electrical Compensation………………………………………………………… | 2.6 |
|  | Compensation Cables…………………………………………………………… | 2.6 |
|  | Buffers………………………………………………………………………….…. | 2.6 |
|  | Pit Switches………………………………………………………………………. | 2.6 |
|  | Stopping Devices………………………………………………………………… | 2.7 |
|  | Travelling Cables………………………………………………………………… | 2.7 |
|  | Electrical Wiring and Control Communication………………………………… | 2.7 |
|  | Automatic Self Levelling………………………………………………………… | 2.7 |
|  | Lift Car Enclosure……………………………………………………………..…. | 2.8 |
|  | Passenger & Goods/Passenger Lift Car Finishes……………………………. | 2.9 |
|  | Fixture Faceplates and Mounting………………………………………………. | 2.9 |
|  | Car and Landing Door…………………………………………………………… | 2.9 |
|  | Lift Door Hangers………………………………………………………………… | 2.10 |
|  | Car Door Control…………………………………………………………………. | 2.10 |
|  | Car Platform………………………………………………………………………. | 2.11 |
|  | Landing Entrances……………………………………………………………….. | 2.11 |
|  | Door Panels………………………………………………………………………. | 2.11 |
|  | Sills and support Angles……………………………………………………….... | 2.12 |
|  | Toe Guards…………………………………………………………………….…. | 2.12 |
|  | Car Position Indicators………………………………………………………..…. | 2.12 |
|  | Car Operating Panel (COP)………………………………………………….…. | 2.12 |
|  | Call Acknowledging Lights……………………………………………………… | 2.13 |
|  | Landing Call Buttons……………………………………………………….……. | 2.13 |
|  | Waiting Passenger Lanterns and Gongs……………………………………… | 2.13 |
|  | Landing Position Indicators…………….……………………………………….. | 2.14 |
|  | Landing Doors and Architrave Finishes.………………………………………. | 2.14 |
|  | Lift Intercom System…………………….………………………………………. | 2.15 |
|  | Load Switches………………………………………………………………….… | 2.15 |
|  | Car Top Requirements………………………………………….………………. | 2.15 |
|  | Special Requirements for Outdoor Escalators……………….……………….. | 2.16 |
|  | Escalator Drive…………………………………………………………………… | 2.18 |
|  | Escalator Control………………………………………………………………… | 2.18 |
|  | Operation with Inspection Control……………………………………………… | 2.18 |

### SECTION 2 – EQUIPMENT REQUIREMENTS

- Hoisting Machine

  - Traction Drive

- The brake shall be spring applied and electrically released by direct current. There shall be two shoes actuated by compression springs. The brake shall have sufficient power to hold the car at any landing with the normal amount of counter balancing and with at least 150% of rated load. The brake shall operate in the event of a power failure or any other safety device designed to stop the lift.

- An effective sound reducing material shall be installed between the bed-plate of an overhead or basement driving machine and the beams, the structural concrete slab, shaft structure or the up-stands.

- The driving machine and motor shall have sufficient capacity to operate the lift continuously at 100% of rated speed in both directions without overheating or hunting during levelling.

- The lift machinery shall operate silently and without vibration. The lifts shall constantly operate and shall be maintained at noise levels not exceeding 56 DB (A). The noise level shall be considered acceptable if it does not exceed 56 DB (A) measured on the landing and in the car enclosure.

- Provision shall be made for a safe method of moving the car by hand in the event of a power failure and all the necessary equipment required to carry out this task shall be mounted neatly in the motor room and shall remain on site at all times.

- The Contractor shall supply and install suitable structural steel beams with bearing plates for the mounting of the lift machine on the motor room floor, as well as supporting beams or deflector and secondary pulleys, as required.  In the cases where machines are located below, the diverter sheaves shall be secured to the floor slabs and not to the overhead slabs, to prevent the transmission of vibration to the structure.

- Anti-vibration mountings shall be provided to minimise the transmission of vibrations to the structure and to ensure the silent and smooth operation of all the equipment. Tenderers shall describe the methods to be used to achieve the desired results.

  - Hydraulic Drive

- An effective sound reducing material / vibration isolation shall be installed between the tank and the motor room walls.

- Provision shall be made for a safe method of moving the lift by hand in the event of a power failure and all the necessary equipment required to carry out this task shall be mounted neatly in the motor room and shall remain on site at all times.

- The lift machinery shall operate silently and without vibration. The lifts shall constantly operate and shall be maintained at noise levels not exceeding 56 DB (A).  The noise level shall be considered acceptable if the noise does not exceed 56 DB (A) measured on the landing and in the car enclosure.

- Oil coolers shall be provided if it is required to maintain an acceptable oil operating temperature.

- The driving machine and motor shall have sufficient capacity to operate the lift continuously at 100% of rated speed in both directions without overheating or hunting during levelling.

- Controller

- Programmable solid state operation and motion controller shall be provided to control the operation, the starting, the stopping and the speed of the lift motor and also to apply the brake automatically if any of the safety devices operate or the power fails.

- All solid state controllers shall be enclosed in ventilated sheet metal cabinets with integral blowers. All power resistors and heat generating transformers shall be mounted in separate enclosures if necessary to maintain the specified control panel internal temperature. The control cabinets shall be totally enclosed, vermin and insect proof, drip proof and dust proof to at least class IP42 of IEC 144.

- Contacts breaking heavy currents shall be provided with magnetic blowouts and arc chutes. Contact surfaces shall be of silver-to-silver except those for heavy currents, where carbon-to-silver or carbon-to-copper contact surfaces may be used.

- All terminals of the machinery and control gear shall be marked with distinctive letters or numbers, and corresponding markings shall appear on the contract drawings.

- All controllers shall be generic manufactured, assembled and supplied.

- As a standard, PLC lift controllers shall not be accepted. However, if these controllers are considered a generic product by the Representative/Agent and are able to meet the requirements of the specification, PLC controllers may be offered as an alternative if the following requirements are met:

- Documentation stating that the control system has been subjected to extensive testing and is verified as safe, reliable and fully complies with SABS 1545 and all national, local regulations and by-laws.

- If requested by the Representative/Agent, the Contractor shall provide the Representative/Agent with a full set of back up software / software module and all associated maintenance related documentation including principle diagrams.

- Documentation from the PLC supplier is provided to verify the age of the model used, the date it is expected to be removed from the production line and the period the PLC supplier will guarantee parts and repairs.

- The Contractor shall verify that the PLC supplier is willing to maintain under a fully comprehensive agreement, the entire PLC unit(s) for at least 20 years.

- Control System

- The control system shall be capable of constantly producing the performance criteria specified.

- The associated control equipment for each control system shall provide smooth acceleration and deceleration.  In conjunction with the controller and machine, the system shall consistently provide the performance times specified.

- The drive control system shall be capable of decelerating the lift to stand still without a “levelling in” or “creeping in” phase. Only lifts with direct floor approach capabilities shall be accepted.

- The motor drive unit shall provide a smooth lift performance including acceleration, steady velocity and deceleration plus levelling to various floors within the time allowance and levelling tolerances specified.  This performance shall be consistent under all conditions of loading and in either direction of travel.

- The motor drive unit shall be equipped with all necessary monitoring circuits to maintain a safe and reliable operation.  These shall include but are not limited to the monitoring of the load, direction of rotation, speed, supply voltage, and operating currents.

- The hoist motor shall be provided with a thermostatically controlled blower if necessary, to dissipate the heat in order to maintain the equipment within the specified operating temperature range.

- The control system shall provide a smooth acceleration and deceleration with the levelling accuracy at all landings from no load to full rated load in the lift.  This smooth operation shall be obtained for all lifts under stable conditions.  A maximum of 0.8 seconds shall be allowed from door close to car start.

- The equipment shall be designed to operate at plus or minus 15% of normal feeder voltage and plus or minus 5% of feeder frequency without damage or interruption of lift service.

- The control system shall be designed to operate the hoist motor continuously at 100% of rated speed and at 100% of rated load in both directions without overheating or hunting.

- Machine Room Indicators / Rope Markers, Monitors and Testing Tools

- Monitor and keyboard or hand held testing instruments for commissioning, re-commissioning and fault analysis of the lift control system shall be provided and shall remain on site at all times. Each group of lifts shall be supplied with its own monitor and keyboard or testing instrument.

- As each lift travels through the lift shaft, a main hoisting rope marker shall indicate its floor level position by means of a mechanical selector attached to the machine control indicator. This indicator shall operate independently to the lift control and shall not be dependent on the lift supply for its operation.

- The lift control system shall be capable of generating error/fault reports. Error logs for each lift showing at least forty (40) of the most recent faults shall be accessible. The error log shall clearly indicate the type of fault, lift number, date and time the fault occurred.

- Safety Gear and Governor

- An over-speed governor, driven directly by an independent rope attached to the car, shall be provided in the motor room and shall be designed to operate the safety gear fitted to the car when the speed of the car, due to any cause, exceeds its normal maximum speed by more than a predetermined value. The tripping speed of the governor shall be selected with due regard to the rated speed. The tripping speed shall be approximately inversely proportional to the rated speed and shall for rated speeds ranging from 0,25m/s to 5,0m/s not exceed the rated speed by more than 40% and 20% respectively.

- The safety gear shall be arranged to stop the lift whenever excessive descending speed is attained.  Means shall be provided to cut off power from the motor and apply the brake prior to application of the safety gear. The safety gear shall be released by moving the lift in the “UP” direction.

- The governor rope system, including the governor and tension sheave, shall be arranged so that the carrier shall not be released due to system dynamics when the lift is subjected to an emergency stop in the “UP” direction.

- Car and counterweight safety gear shall be provided with a switch to cut off the power from the motor and apply the brake, if the safety gear applies without tripping the governor.

- Rope guards and an electrical contact to monitor the rope stretch shall be provided on the governor tension sheaves.

- Rope Guards

Rope guards shall be used to cover machine sheaves, secondary or deflector sheaves and governor sheaves to cover moving sheaves and ropes. Guards are also required on rope hole openings in the machine room and secondary level floors to prevent objects from falling into the lift shaft. Guards shall be provided in secondary level floors where ropes and tapes or selector drives pass through to prevent accidental contact.

- Motor Room Ventilation and Lighting

- The Lift Contractor must ensure that the lighting levels and ventilation of the machine room provided are sufficient.

- If any alterations have to be made the Lift Contractor must inform the Representative/Agent in writing, to ensure that it will be corrected.

- Machine Data Submittals

The Contractor shall supply all the relevant machine data to ensure the correct power feeder design, including, but not limited to the following:

-	Lift numbers

-	Capacity / load	kg

-	Speed	m/s

-	Supply Voltage	Volts

-	Supply Frequency	Hertz

-	Number of wires

-	Motor kW rating	kW

-	Roping

-	Full load UP acceleration	Amps

-	Full load UP nominal speed	Amps

-	Machine heat release per car	BTU/hr/car

-	Power Factor	%

- Lift Shaft Requirements

- In terms of SABS 1545 (Parts 1 and 2) provide the necessary rope or selector tape guards in pit areas and landing door unlocking devices on all landings.

- Provide safe Working Platforms in pits with depths in excess of two (2) metres and if necessary at the top of the shaft to create sheave-room platforms.  The working platforms shall comply with SABS 1545 (Parts 1 and 2) safety requirements pertaining to the depth/height and free space of these areas.

- In terms of SABS 1545 (Parts 1 and 2), shaft lights are to be provided and installed by the Contractor.

- Car and Counterweight Guide Rails

- The guide rails for the car and counterweight shall consist of planed steel tees with milled, tongued and grooved joints. Metal splice plates shall be of a suitable length and fixing brackets for guide rails shall be provided at intervals not exceeding 2,4m.  Guide rail fixings shall be located in such positions that when the car is at any landing, the guide shoes on the car will be at a fixing bracket. The bottom end of each guide rail shall be provided with a sole-plate fixed to the pit floor.

- All brackets shall be secured by means of approved expandable concrete anchor bolts of adequate size and length.

- Hoist and Governor Ropes

- The ends of the hoist ropes shall be properly secured to the car and counterweight cross-head or to the dead-end hitch plates on 2:1 roping, with adjustable rope shackles having approved sockets. Screw adjustment shall permit equalisation of the tension in all ropes.

- The lift car hoisting rope attachment / hitch shall be suitably vibration isolated to prevent rope noise from being transferred to the car enclosure.

- Governor ropes shall be in accordance with SABS 1545 (Parts 1 and 2) and the steel rope shall be specially designed for lift service. The two ends shall be securely fastened together at the lift and shall be attached to the safety operating mechanism. The governor rope shall pass over the governor sheave and over an approved tensioner sheave in the pit. An electrical contact shall be fitted to the pit sheave and shall stop the lift if the governor rope becomes slack or breaks.

- Counterweight

- Each lift shall be suitably counterbalanced for smooth and economical operation. Cast iron or steel sub-weights shall be contained in a guided structural steel frame. The counterweight shall be equal to the weight of complete lift car plus at least 40% of the rated load.  The weights in the counterweight frame shall be balanced with the weight equally distributed across the width of the frame to equalise guide pressures. The sub-weights shall be welded or fastened together as necessary to prevent rattling.

- Counterweight screen guards shall be provided at the bottom of the shaft to a height of 2150mm above the floor of the pit and approximately halfway up the shaft at the position where the car and counterweight pass each other.

- Car and Counterweight Guide Rollers or Shoes

The car and counterweight guide rollers/shoes shall constantly provide the ride quality as specified in Section 3 clause 11 of this specification.

  - Guide Rollers

- Each lift shall be provided with car and counterweight rollers guides. Each roller guide shall consist of at least three wheels with a durable resilient material, each rotating on ball bearings having sealed-in lubrication, assembled on a substantial metal base and so mounted as to provide continuous contact of all wheels with the corresponding rail surface under all conditions of loading and operation. The wheels shall run on three machined rail surfaces. The roller guides shall be properly secured at top and bottom on each side of the car frame and counterweight frame.

- The roller guides shall run on dry guide rails. Sheet metal guards shall be provided to protect wheels located on the top of the car and the counterweight. The roller wheels for the car shall not exceed 500-rpm and the roller wheels for the counterweight shall not exceed 1000-rpm at rated speed.

  - Guide Shoes

If the speed and load nominated for a specific lift allows the use of guide shoes:

- The lift shall be provided with car and counterweight spring loaded guide shoes. The spring tension shall be adjusted so as to maintain the lift in the centre of the rails and provide continuous contact with the corresponding rail surface under all conditions of loading and operation. The guide shoes shall be lined with a durable resilient material, which shall ensure a quite and smooth ride. When oil buffers are attached to the bottom of the counterweight, additional guide shoes shall be installed on each side of the buffer cylinder frame.

- The guide shoes shall run on lubricated rails. The guide rails shall be lubricated by a permanently mounted lubrication reservoir on top of the car and counterweight.

- Electrical Compensation

A sufficient extra hoisting kilowatt rating in the hoist motor, machine and motor generator capacity and control equipment may be provided so that effective electrical compensation for the weight of the hoist ropes and travelling cables shall be accomplished as the lift travels through the lift shaft.

- Compensation Cables

If Section 2 clause 14 (Electrical Compensation), cannot be achieved the following shall apply:

- Compensating trailing cables or compensating chains encased in a synthetic sleeve (whisper flex) shall be provided.

- Compensating cable restraining rings shall be provided in each pit and mounted on both the car and the counterweight buffer supports.

- Compensation shall be fixed to the bottom of the counterweight and car in a position which shall allow the counterweight to remain balanced in the guides and exert equal pressure on each face of the guide at the four guide locating positions.

- The fixing of the compensation to the car shall be accomplished by a vibration isolating compensation hitch.

- Where compensating steel ropes are used for compensation they shall be accompanied by a statically balanced compensation pit sheave and shall be mounted centrally between the guides.

- Buffers

- Suitable oil, heavy spring or polyurethane buffers shall be provided for the car and counterweight and shall be so adjusted that in the case of over-travel, no parts of the car or counterweight will touch the shaft ceiling and that the retardation of the car does not exceed the limits as laid down in the SABS 1545

- Hydraulic buffers shall be so constructed and shall be installed to allow the fluid level to be checked easily. Easy access to the buffer for testing and maintenance purposes shall be possible without having to remove the counterweight pit screen.

- Energy dissipation type buffers shall have an electrical contact fitted to monitor the stroke (extended position).

- Pit Switches

Each lift pit shall be provided with watertight pit safety switches accessible from the entrance to the pits without the necessity of entering the pit and shall also be accessible from the pit while standing on the pit floor. The pit switch shall interrupt the power supply and apply the brake to hold each car so as to permit safe access to the pit. The pit switch shall be clearly distinguished from other switches that may be mounted in the pit area and the on/off position shall be clearly marked.

- Stopping Devices

- Normal terminal stopping devices shall be enclosed in dust-proof enclosures for each lift. These devices, once operated, shall bring the lift automatically to a smooth stop at the terminal landing.

- Final terminal stopping devices shall be positioned at the top and at the bottom of each lift shaft. A fixed cam securely attached to the lift shall operate these final limit switches. These limit switches shall be independent of any other stopping devices and shall positively open without the use of springs to cut off all power from the driving machine motor and brake.  It shall prevent the operation of the lift in either direction.  They shall be so located that they open at the time the lift or the counterweight engages the buffer.

- Travelling Cables

- Travelling cables between the lift and the fixed lift shaft wiring shall be flexible and suitably suspended to relieve the strains in the individual conductors. All cables shall contain an approximately equal number of conductors, or shall have equal flexibility.

- Travelling cables shall include two shielded pairs for each lift car to accommodate voice communication.

- The travelling cables shall be positioned in such a manner to eliminate the possibility of interference with the shaft information, selector tape or governor rope and all the necessary travelling cable protection shall be fitted to the shaft wall and shaft trimmers to prevent damage to the outer cover during normal travel.

- The travelling cables shall be neatly and adequately strapped to the side of the car enclosure and all the necessary protection shall be provided where the cables cross over metal extrusions.

- Travelling cables for the counterweight shall comply with the requirements of this section.

- Flat and round trailing cables shall be fixed and shall hang in accordance with the trailing cable manufacturer's requirements.

- Electrical Wiring and Control Communication

- All low voltage and control communication cables shall be run in separate ducts, conduits and trailing cables.

- Car top terminal boxes of ample size and car top inspection control units shall be provided.

- Automatic Self Levelling

All lifts shall be provided with both a self levelling and a re-levelling feature that shall automatically bring the lift to the floor landings within a tolerance of 3.0 mm under no load to full rated load conditions without hunting. Self levelling shall, within its zone, be entirely automatic and independent of the operating device and shall correct over-travel and rope stretch.  The lift shall be maintained level with the landing, irrespective of load and while loading and unloading.

- Lift Car Construction and Enclosure

- The lift car shall be an assembly consisting of the sling, the platform and the cabin.

- The sling shall be constructed of rolled steel angle or channel sections bolted or welded together to form a rigid framework, which shall be suitably braced and reinforced to withstand the operation of the safety gear without permanent distortion.

- The car platform shall consist of  a 3mm thick mild steel plate or 20mm thick hardwood floor laid on closely spaced steel channel sections welded to a steel frame which in turn shall be laid on rubber pads in a structural steel frame. Load weighing devices shall be incorporated where specified.

- The cabin shall be designed as a fully enclosed car with a flat roof and solid full height panels on the sides and the back.

- The cabin shall be securely fixed to its sling and platform in such a manner that the cabin is not subjected to strain in the event of an unequal distribution of load occurring over the floor area.

- The entire car assembly, including the car frame and the car platform shall be constructed to operate free from objectionable squeaks or metallic sounds, comprising of a rigidly tuned resonance car frame and acoustically treated superstructure.

- The following features shall also be embodied in the lift car:

- A continuous lighting system shall be provided along each side of the car. The lighting system shall consist of concealed, surface mounted, standard 2-lamp open fluorescent luminaires, providing an illumination level of not less than 200 lux at 1000mm above floor level. Fluorescent tubes shall be 1500mm, 58 Watt or 1200mm, 36 Watt, colour "Warm White". Tubes and control gear shall be of the switch start type and shall bear the SABS mark. The width of the lighting troughs shall be the same as the front return panels and shall be covered by easily removable low brightness diffusers, mounted in purpose made hinged frames.

- One of the lamps in each trough shall be provided with an emergency battery/inverter unit by means of which the lamp will be operated for at least 60 min. in the event of a power failure. This lamp shall operate at full output under normal conditions.

- Luminous car position indicator and "Up/Down"" travel indicators installed above the entrance doors.

- Fixing clips for the attachment of canvas protective coverings which shall be supplied with the lift for the side and rear walls.

- Silent running squirrel cage, centrifugal flow exhaust blowers for passenger and goods/passenger lifts shall be mounted to draw air into car enclosure when doors are open and through door side clearances when door s are closed. The blower shall be mounted on the car top, draw air from the car through the perimeter of the suspended ceiling and exhaust the air into the lift shaft. The fan shall without exception, be capable of delivering not less than 0.3 cubic meters of free air per minute per square meter of floor area. The fan shall be switched via a toggle switch mounted in the car operating panel.

- Lift Car Finishes

Lift car finish detail shall be as specified in section 4 of this document.

  - Passenger & Goods/Passenger Lift

- The entire car internal finish including the area above the suspended ceiling shall be installed and finished off to the highest standard. All finished work shall be smooth and free from wraps, buckles, squeaks and rattles and all joints shall be light-proof.

- All wall panelling shall be jointed with a pliable material /silicone to prevent squeaks generated by car panel movement / deflection.

- A robust handrail, consisting of an “Intrad” poly-carbonate bumper tail, spaced 50mm off the panelling, must be provided across the rear and side walls of the lift car. The spacer blocks to which the hand and bumper rails are secured shall be fixed to the panels by means of  2 x M10 bolts with locknuts or other approved method.

- A silvered glass mirror shall be provided at the rear of the cabin in the side walls between the hand rail and the ceiling.

- Goods/Passenger lift car panels shall be manufactured from at least 1.5mm mild or stainless steel with at least two horizontal intermediate stiffening ribs and panels with a width greater than 400mm shall have vertical stiffening ribs at intervals not exceeding 200mm or equivalent construction.

- Fixture Faceplates and Mounting

- Unless otherwise specified, all landing fixture faceplates shall be surface mounted and shall be manufactured of at least 3.0 mm thickness stainless steel, with bevelled edges for all lifts if square rectangle stainless steel face places are offered.  However, Contractors may offer alternative landing fixture face plates if these faceplates are generic products and aesthetically acceptable to the Representative/Agent.

- The fixture faceplates in the lift car and at the landings shall be mounted with concealed security fastenings or fastenings requiring special tools to remove them, as approved by the Representative/Agent. Exposed fastenings shall match the material and finish of the faceplate.

- The following fixture face plates shall be located and sized in accordance with dimensions approved by the Representative/Agent:

-	Car operating panels.

-	Car position indicators.

-	Car direction indicators.

-	Landing push button stations.

-	Landing position indicators and signals.

-	Blanking-off plates

- Without exception the Representative/Agent shall approve the final design of the fixture faceplates before placing the order or manufacturing of this equipment.

- Car and Landing Door Operator

- Only door operators with the capabilities of coping with medium to heavy traffic shall be accepted and the type of door operator offered shall be clearly shown in the tender submitted. The door system shall be capable of controlling the position of the doors at any given moment and shall constantly produce a smooth, accurate and efficient operation.

- The doors on the lift car and at each landing opening shall be opened and closed quietly and smoothly by an electric operator.

- The motion of the door operator shall be accomplished with arms and appropriate linkages to the approximate centre of gravity of the driven door panel.

- Each landing door shall be equipped with Electro-mechanical interlocks so that the lift can operate only when the interlock circuit is established. Landing door locks shall meet the SABS 1545-1 safety requirements.  All work and material related to this Sub-Section shall from part of the Contractor’s scope of works.

- An independent auxiliary self-closing device shall close each landing door panel whenever the door is not in the closed position and the equipment relating to the car and landing door system does not restrain it.

- An electric contact for the lift car door shall be provided which shall prevent the lift moving away from a landing unless the door is in the closed position.

- An electrical contact shall be fitted to the non-driving car door if its linkage is dependent on a wire rope or chain.

- Emergency Triangle access key mechanisms shall be provided on each entrance.

- Lift Door Hangers

Hangers shall be equipped with ball bearing adjustable rollers to take the up-thrust of the doors. The hangers and rollers shall be designed to accommodate the size and weight of the doors operated with a high speed door operator.

- Car Door Control

27.1	Car Door Motion Controllers

- Car door motion controllers dependent on resistors, rheostats or switches to control the opening and closing motion shall not be accepted.  The car door motion controller shall be capable of controlling the position of the doors at any given moment and shall constantly produce a smooth, accurate and efficient operation.

- (For Group controls only) Adjustable hardware or software timers shall be provided to hold the doors open for the dwell times specified below.  The tabulated dwell times are initial adjustment standards. Further adjustment to suit specific traffic movement capabilities and the arrangement of car and landing stations shall also be possible.  The first passenger dwell times are those measured from door fully open to door start-to-close.  The second and succeeding dwell times are from restoration of the light beam to door start to close from its fully reopened position.

Passenger 			Stops for 		Stops for

Conditions 			Car Call	 	Landing Call

----------------------------------------------------------------------------------------------

First Passenger 		2.0 sec. 		3.0 sec.

Succeeding Passengers 	1.0 sec. 		1.0 sec.

----------------------------------------------------------------------------------------------

Stops at the high or low car call reversal floors shall be considered as landing call stops.

- If doors are held open for an adjustable period of time by a passenger standing in the entrance or by constant pressure of the door open button, a buzzer shall sound and the doors shall start to close at a reduced speed and force level.  When the doors touch an obstruction, they shall re-open.

27.2	Door protection devices

- A non-retractable electronic infra-red/ultra-sonic protective leading edge shall be provided and shall extend at least 2100-mm above the platform and its active surface/area shall project beyond the front edges of each leading car door panel. Should this device come in close proximity, or touch a person or object whilst the car doors are closing, the car and shaft doors shall return to their open position.  Manual reversal of the doors while the lift is on automatic operation shall be accomplished by pressing a door open button in a car-operating panel. Should this device be activated while the car doors are closing, the car and shaft doors shall return to their open position.

- Without exception the Contractor shall demonstrate on the day of Completion that the door closing pressures comply in full with the SABS 1545 Part 1 and Part 2 under normal and forced closing conditions.

- The door protection device shall have the capabilities of detecting metal/plastic trolleys.

- Car Platform

The car platform with enclosure of each lift shall be balanced by arranging balancing weights to equalise the guide pressure (front to back and side to side) so that the pressure on any guide shoe roller does not exceed 18kg without load in the car. (Statically balanced).

- Landing Entrances

(a)	Each lift shaft landing entrance assembly shall consist of unit frame, door panels, fascia, sill, hanger, closer and interlock. The installation shall comply with the applicable code requirements.

(b)	As a standard all lift landing equipment including doors, signal faceplates shall have a two (2) hour fire rating.  The Contractor shall provide the relevant SABS test certificates for Class “C” type landing door equipment.

- Door Panels

- The door panels for all openings shall be constructed of at least 1.5 mm thick mild or stainless steel. Continuous stiffener channels must be provided to the top, bottom and edges at the faceplates. The bottom of each door panel shall be provided with removable laminated phenolic guides, which run in the sill slots.

- Door panels shall be constructed to operate free from squeaks or metallic sounds and shall be adequately treated with a sound deadening material to produce a quiet door operation under all operating conditions.

- The leading edge of the car and landing doors shall have an interlocking profile with rubber stoppers (top and bottom) to prevent the door panels closing metal to metal.  Add on rubber profiles shall not be accepted.

- All landing door site guards shall have a stainless steel box type construction for added rigidity.

- Goods/Passenger Lift and Access, Goods Only Lift Car Doors

- Car and landing sills shall have additional angle iron supports (reinforced sills) to accommodate the applicable point loads.

- Landing and car door panels shall have reinforced sliding shoe supporting sections.

- Only reinforced sliding door panels shall be accepted.  Door panels shall be at least 1.5 mm thick Mild Steel or Stainless Steel with at least two horizontal intermediate stiffening ribs.

- Sills and Support Angles

The landing sills for all openings shall be of narrow extruded aluminium.  Grooves in all sills for the door guides shall be machine planed with minimum clearances for the guides. The sills shall be supported on steel angles provided by the lift Contractor and securely fastened to the building floor construction.

- Toe Guards

Toe guards shall be of at least 1.5 mm thick steel and shall be installed on all landings.  They shall extend the full width of the door opening and be gradually bevelled to the wall.  The straight vertical portion of the guards shall at least be 400 mm long or as in the case of the lowest landing shall equal the distance travelled by the car sill from the bottom terminal landing to when the car is on the fully compressed buffer.

- Car Position Indicators

(a)	Electronic LED digital readout position indicators shall be incorporated in each lift car operating panel at a height of not less that 2100 mm above the floor.  As each lift travels through the lift shaft, its position shall be indicated continuously by the illumination of the numeral or letter corresponding to the landing that the lift is stopped at or is passing.

(b)	The digital readout shall be at least 50 mm in height.

- Car Operating Panel (COP) for Passenger and Goods/Passenger Lifts

- The operating device for each lift shall include a series of buttons, numbered to correspond to the active landings served and various additional buttons and key switches, including emergency alarm, intercom, door open and door close buttons, independent control, fire control and rear door control key switches.

- The car call buttons shall be numbered to correspond to the landings served or the numbers shall be engraved with recessed background adjacent to the car buttons.

- Car, landing and emergency buttons shall be of the Micro push operation type and shall be approved in terms of the Occupational Health and Safety Act. Each button shall be clearly marked with its corresponding floor position.  The demarcation shall either comprise a raised or recessed numeric or alphabetic character. Car call buttons shall have Braille incorporated into the button unit.

- The car operating station shall be paraplegic friendly and shall be located so that all operating and emergency buttons are located between 1500 mm and 900 mm above the car platform. The emergency buttons and switches shall be mounted at the bottom and the call buttons in numerical order starting above the emergency button and numbering from left to right.

- Swing front return panels used in the passenger car enclosures shall be arranged so that the call buttons and the control and signal devices are substantially flush to the vertical surface and shall be mounted on the return panel.  The wiring to the individual components shall permit the panel to swing open for maintenance purposes.

- A second rear door car-operating panel for lifts with two entrances shall operate independently to the front panel and shall comply in full with this section.

- As a standard the lift signage shall include No Smoking, Load, Passengers, Certificate Number and Lift Number / Designation, as required by the applicable standards and regulations. All signage shall be engraved into the Car Operating Panel.

- Without exception the Representative/Agent shall approve the final design of the car-operating panel before placing the order or manufacture of this equipment.

- The number of Car Operating Panels per lift shall be as nominated by the Representative/Agent.

- The button markings/engraving shall be such that it does not fade or wear with continuous operations. The markings, whether engraved or raised shall remain clearly visible and the coloured epoxy shall remain intact throughout the life of the button.

- All key switch cylinders in the fixture faceplates of landing stations, car stations and supervisory control stations shall be master keyed with removable core cylinders (KABA type or equivalent).

- Call Acknowledging Lights

All car and landing buttons shall be of the call acknowledging type. The registering of a call button shall illuminate the button to acknowledge that a call has been registered.  Incandescent indicator lamps shall not be accepted.

- Landing Call Buttons

  - Passenger and Goods/Passenger Lifts

- A riser of landing micro push button stations shall be provided. Terminal floors shall contain a single button station and intermediate floors shall contain both up and down buttons. Pressure on the button in one fixture shall cause the electronic illumination of the corresponding button unit in the other fixture at the same landing.  Incandescent button illumination shall not be accepted.

- Landing push buttons shall be of the Micro push operation type and shall be approved in terms of the Occupational Health and Safety Act.

- The location of the centreline of each landing micro push button fixture shall be located at 1050 mm above the floor.

- Each button shall be clearly marked with its corresponding direction of travel.  The demarcation shall either comprise a raised or recessed approved symbol.

- The button markings/engraving shall be such that it does not fade or wear with continuous operations.  The markings, whether engraved or raised shall remain clearly visible and the coloured epoxy shall remain intact throughout the life of the button.  Buttons shall have Braille incorporated into the button unit.

  - Access Goods Only Lifts and Dumbwaiters

- Refer to Section 3, clause 1.2 of this document.

- All buttons shall be micro-push buttons.

- Waiting Passenger Lanterns and Gongs

- Provide an up and down, LED digital readout electric indication waiting passenger lantern at each intermediate landing and an up or down single indication lantern at a terminal landing of all lifts. The lanterns shall be mounted above the head jamb or beside the side jamb of each typical entrance.  Incandescent indicator lamps shall not be accepted.

- Supply and fit adjustable electronic arrival gong to each entrance. The fixture face plate shall contain an approved pattern of slots to enable the transmitting of the sound from within the shaft to the lift foyer.  In terms of the paraplegic/blind person’s requirements the gongs shall have a different tone when announcing cars travelling in the up and down directions - two “gongs” for down and one “gong” for up.

- As soon as a lift has reached a predetermined distance from a landing and is going to stop at that landing, the corresponding waiting passenger lantern shall be illuminated and the gong shall sound whether or not a landing call has been registered. The waiting passenger lantern shall remain illuminated until the lift leaves the landing or if the car becomes filled, whichever occurs first.

- The type and design of the landing signals shall take into account long lift lobbies associated with groups of lifts installed adjacent to each other. After installation the landing direction and/or announcing arrows shall be clearly visible from any position within the lift lobby.  It shall be the Contractor’s responsibility to inform the Representative/Agent if the selection of landing signal design is not going to achieve the visual requirements detailed under this section.

- As an exception and if specifically requested by the Contractor and accepted in writing by the Representative/Agent, adjustable gongs may be fitted to the car. Gongs fitted to the car shall be positioned in the header section of the car and the sound shall be contained and directed towards the entrance so as not to be transmitted to the floors above and below the lift. The gongs shall further only sound when the lift is within 200 mm from the landing level.

- As an exception and if specifically requested by the Contractor and accepted in writing by the Representative/Agent, announcing arrows may be fitted in the side jambs or incorporated in the push button unit. However, this option shall be restricted to Simplex and Duplex units with a single riser of buttons.

- Landing Position Indicators

- Electronic LED digital readout position indicators shall be provided over the architrave of each lift in the main lift lobby.  As the lift travels through the lift shaft, its position shall be indicated continuously by the illumination of the numeral or letter corresponding to the landing that the lift stopped at or is passing.

- The final number of landing indicators required for each lift and their locations shall be as approved by the Representative/Agent.

- The digital readout shall be at least 50 mm in height.

- Landing position indicators shall not illuminate if the lift can no longer respond to calls as a result of a fault condition or when undergoing routine maintenance.

- Landing Doors and Architrave Finishes

(a)	All stainless steel landing doors and architraves shall be cleaned prior to final acceptance and receive a coat of an approved stainless steel polish.

- When spray painting the landing doors and frames, the Contractor shall ensure that the landing door panels are satisfactorily prepared before the final coat of Duco is applied.

- Floor designation shall be permanently marked on the inside of the landing doors (shaft side).

- Lift Intercom System

Only if Specified in Section 4 of this Specification

- Provide an intercommunication system complete with talk-back speakers with all required auxiliary equipment, wiring and a six (6) hour minimum back-up power supply.

- Lift travelling cables shall contain two (2) shielded pairs of conductors for each car for the intercommunication system.

- Terminal strip boxes for all wiring shall be provided.

- All wires in the wiring system shall be shielded without exception.

- Wiring between all master stations in the building shall comply with manufacturer's recommended standards.

- Provide one sub-station in each lift car, one master station for each motor room and one master station for the security control room.

- The voice link shall constantly produce a sound/speech quality comparable to that of the normal Telkom telephone network. All provisions to adequately address interference in the lines shall be included. The intercom master stations shall include an indicator system/panel to indicate the lift car initiating the emergency call and an “All Call” feature to allow for communication to all lifts at the same time.

- The lift intercoms for all the lifts shall be wired back to a common security/control room centrally located.

- The Master Stations shall be capable of accommodating all the lifts covered under this Specification. The individual lift’s designation and its call code shall be clearly and neatly displayed on the Master Station.

- Load Switches

All load switches and sensors which influence the control and the drive shall be adjusted in order to achieve an optimum operation, and their operating loads documented for future reference on the data sheet or certificate of compliance SABS1545 - Annex “A”.  These load contacts may include but are not limited to the over-load, minimum load and the landing call by-pass functions.

- Car Top Requirements

42.1	Car Top Working Platform

Securely fitted working platforms of adequate strength shall be provided on the top of the car roof to create a level and safe working area.  The platform shall be free of any electrical cabling and lift equipment.  The car roof shall not be regarded as a working platform.

42.2	Car Top Guard Rails

In terms of SABS 1545 the car top shall be provided with a balustrade (guard-rail) where the free distance in the horizontal plane beyond and perpendicular to its outer edge exceeds 300 mm.

- Special Requirements for Outdoor Escalators

43.1	Outdoor Escalators - Covered

Undercover outdoor escalators are escalators with a roof and optional lateral cladding so that neither snow nor rain can reach the unit under normal circumstances.  Any moisture that gets tracked onto the unit by shoes will not impair the serviceability.

The following special design elements does not limit or restrict the Contractor from providing the additional special design elements/requirements in terms of the manufacturers recommendations applicable to outdoor covered escalators.  The Contractor shall remain responsible to supply all the recommended special design elements applicable to the escalators covered under this specification.

Outdoor covered escalators without exception, shall incorporate the following related design elements:

- 1.0 mm stainless steel motor covers

- 1.0 mm stainless steel drive-chain covers

- Water Drain Truss

Outdoor escalators shall have a water drain truss.  The water drain is accommodated in the return station and should be installed in tandem with oil separators.  A water level contact with an audible alarm shall be provided to protect the escalator against flooding in the return station.  The water level contact must be supplemented with a pump installed and supplied by the Employer.

Before the water level in the pit rises to a point where it can cause damage to the escalator equipment, or, to a point where the water can be picked up by the rotating steps, the level switch shall activate an audible buzzer/alarm.  After a further rise in the water level the escalator travel shall be blocked.

(b)	Special Design Elements

- An increased anodising layer shall be provided for all aluminium profiles.

- Lateral cladding on both sides of the escalator shall be provided.

- The escalator motor system shall be IP55 rated.

- The escalator electrical system shall be IP54 rated.

- Balustrade skirting shall be Stainless Steel – Grain 240.

- The escalator truss shall be painted with an approved corrosion inhibiting/protection paint (Grey).

- Step chains shall be provided with sealed rollers.

- Step axles shall be stainless steel.

- Automatic lubricating systems and oil drain channels shall be provided.

- Stainless steel drive unit covers shall be provided.

- Stainless steel drive chain covers shall be provided.

- Step chain covers shall be provided.

- Handrail guide profiles shall be stainless steel.

- Increased corrosion protection (Grey) for the escalator track system and (Yellow) for all rotating parts.

43.2	Outdoor Escalators - Uncovered

Uncovered outdoor escalators are escalators exposed to the elements.

The following special design elements does not limit or restrict the Contractor from providing the additional special design elements / requirements in terms of the manufacturers recommendations applicable to Outdoor Uncovered Escalators.

The Contractor shall remain responsible to supply all the recommended special design elements applicable to the escalators covered under this specification.

Outdoor uncovered escalators exposed to the elements shall without exception, shall incorporate the following related design elements:

- 1.0 mm stainless steel motor covers.

- 1.0 mm stainless steel drive-chain covers.

(a)	Water Drain Truss

Outdoor escalators shall have a water drain truss.  The water drain is situated in the return station and should be installed in tandem with oil separators.  A water level contact with an audible alarm shall be provided to protect the escalator against flooding in the return station.  The water level contact must be supplemented with a pump installed and supplied by the Employer.

Before the water level in the pit rises to a point where it can cause damage to the escalator equipment, or, to a point where the water can be picked up by the rotating steps, the level switch shall activate an audible buzzer/alarm.  After a further rise in the water level the escalator travel shall be blocked.

(b)	Reinforcement for Wind Exposure

When installing escalators outdoors, wind loads shall be considered.  It shall be the responsibility of the Contractor to obtain all the relevant information regarding the maximum wind velocity and wind direction to properly dimension the escalator truss.

(c)	Special Design Elements:

The following elements shall be provided:

(i)	An increased anodising layer shall be provided for all aluminium profiles.

- Lateral cladding on both sides of the escalator shall be provided.

- The escalator motor system shall be IP55 Rated.

- The escalator electrical system shall be IP54 Rated.

- Balustrade skirting shall be Stainless Steel – Grain 240.

- The escalator truss shall be painted with an approved corrosion inhibiting/protection paint (Grey).

- Step chains shall be provided with sealed rollers.

- Step axles shall be stainless steel.

- Automatic lubricating systems and oil drain channels shall be provided.

- Stainless steel drive unit covers shall be provided.

- Stainless steel drive chain covers shall be provided.

- Step chain covers shall be provided.

- Handrail guide profiles shall be stainless steel.

- Increased corrosion protection (Grey) for the escalator track system and (Yellow) for all rotating parts shall be provided.

43.3	Waterproofing of Escalator Pits

It is assumed that water may penetrate down the side of the escalator truss cladding and enter the pit area.  It shall be the Contractors responsibility to inform the Representative/Agent of all escalator pit waterproofing requirements and the pit dimensions given and drawings issued must clearly detail the pit waterproofing requirements.

- Escalator Drive

Escalators shall include the soft-start feature incorporating an adjustable uniform acceleration curve thereby insuring a comfortable ride and limiting mechanical wear on components when the escalator is in automatic mode (stop-and-go operation).

The motor drive unit shall be equipped with all the necessary monitoring circuits to maintain a safe and reliable operation.  These shall include but are not limited to, the monitoring of the load, direction of rotation, speed, supply voltage and operating currents.

The equipment shall be designed to operate at plus or minus 15% of the normal feeder voltage and plus or minus 5% of the feeder frequency without damage or interruption of escalator service.  Protective devices shall be included to prevent damage on over- or under-voltage.

The control system shall be designed to operate the Escalator continuously at 100% of the rated speed and at 100% of the rated load in both directions without overheating or stalling.

- Escalator Control

Escalator control systems shall be Computer Based with self-diagnostic and fault analysis capabilities.

Error Logs showing at least forty (40) of the most recent faults shall be accessible.  The Error Log shall clearly indicate the type of fault, escalator number, date and time the fault occurred.

- Operation with Inspection Control

A Remote Inspection Control unit for maintenance purposes shall be provided and shall remain in the escalator Motor Room or pit at all times.  The operating buttons shall be of the continuous pressure type and the inspection speed of the escalator shall be 50% of the nominal speed.

SPECIFICATION FOR THE INSTALLATION OF

# LIFTS, ACCESS GOODS LIFTS ONLY AND ESCALATORS

SECTION 3 – OPERATIONAL REQUIREMENT

## TABLE OF CONTENTS

| Clause |  | Page |
| --- | --- | --- |
|  | Simplex Selective-Collective Automatic Operation…….…………………….. | 3.1 |
|  | Group Automatic Operation – Two or More Lifts in a Group…….…..……… | 3.2 |
|  | Operation with Independent Service…………………………….…………….. | 3.4 |
|  | Operation with Inspection……………………………………..………………… | 3.4 |
|  | Emergency Operation………………………………..………….………………. | 3.4 |
|  | Fireman’s Operation……………………………………………...……………… | 3.5 |
|  | Operation wit Standby Power……………………..……………………………. | 3.6 |
|  | Door Operation and Control……………………………..……………………… | 3.6 |
|  | Overload Protection…………………………………….……………………….. | 3.7 |
|  | Drive Control……………………………………………………………………… | 3.7 |
|  | Ride Quality and Performance Criteria…………………….………………….. | 3.7 |

### SECTION 3 – OPERATIONAL REQUIREMENTS

- Simplex Selective-Collective Automatic Operation

  - Passenger & Goods/Passenger Lifts

(a)	The operation of lifts shall be from the landing buttons and from the call buttons in the car-operating panel. Single call buttons shall be mounted at each terminal landing and "up” and "down" buttons at each intermediate landing.

(b)	The operation shall be such that momentary pressure on one or more car or landing buttons, other than those for the landing at which the lift is standing, shall start the lift, provided the interlock circuits are established and cause the lift to stop at the first landing for which a car or landing call is registered corresponding to the direction calls registered and these stops shall be made in the order in which the landings are reached, irrespective of the sequence in which the calls are registered provided the call for a given landing is registered sufficiently in advance of the arrival of the lift at that landing to permit the stop to be made.

(c)	If there are no car calls and the lift starts up in response to several down calls, the lift shall proceed to the highest down call and then reverse to collect the down calls.  Up calls shall be collected similarly when the lift starts down in response to such calls.  If the lift stops for a landing call the direction of travel shall be anticipated and maintained for a predetermined interval and independent of additional car and landing calls registered in the opposite direction of the anticipated travel.

(d)	If down landing buttons are pressed while the lift is travelling up, the lift shall not stop at these landings, but these calls shall remain registered.  After the highest car and landing calls have been answered the lift shall reverse automatically and respond to car and landing calls registered below the lift.  When travelling down, the lift shall not respond to up landing calls, but these calls shall remain registered and be answered on the next up trip.

(e)	After the lift has answered the last call and after a pre-set time period, normally 20-seconds, the lift shall be dispatched to a nominated Boarding Floor. Provision must be made to have this automatic return feature disabled if required.

  - Access Goods Lifts Only and Dumbwaiters

(a)	Each landing shall be provided with the number of buttons corresponding to the number of landings served.

(b)	The lift shall have a call and send operation. The lift shall respond to one call at a time and this call shall be the first call registered.

(c)	As the lift arrives at a landing a gong or buzzer shall sound for an adjustable time. The adjustable time shall be pre-set to 30 seconds.

(d)	Should the lift be standing at a landing with open doors and it is called from another floor, a gong or buzzer shall sound on the landing that the lift is standing for an adjustable time before the doors close and the lift moves to answer the call. The adjustable time shall be pre-set to 30 seconds.

- Group Automatic Operation – Two or More Lifts in a Group

  - Automatic Operation

- The operation of passenger lifts shall be group automatic operation arranged, dispatched and controlled by a group supervisory system. The system shall be supervised by a re-programmable minicomputer or microprocessor system.

- Each lift shall be arranged for automatic operation without attendant through the car and landing buttons in conjunction with a group supervisory system that is re-programmable by the replacement of pre-programmed EPROM’s.  This re-programming shall be possible without making changes to the lift hardware or shaft or machine room fixed wiring.

- Group, lift, car and drive control commissioning parameters shall be software “switches” and it shall be possible to fine tune these variables using a permanently installed terminal or test tool.

- The starting of a lift shall be contingent upon the establishing of its door interlock circuit.  The lifts shall automatically slow down and stop level at the floors in response to car and landing calls.  A landing call shall be automatically cancelled as the lift slows down and while stopped to prevent other lifts from responding to the same call.

- Whenever a lift is returned to group automatic operation after being operated on for inspection, independent, or firemen service, the lift shall immediately take its place in the group.

- Car doors shall be prevented from closing or may be reversed while closing by the electronic door control system, the protective leading edge on the car door or by pressing the door open button in the car operating panel.

- The door open dwell times shall be software adjusted so that the open time for a car call is shorter than that for landing calls.

- All car and landing calls shall be cancelled as they are answered.

  - Group Supervisory System

Each group of lifts shall be provided with a software programmable automatic supervisory group system arranged to co-ordinate effectively the movement of the individual lifts of the group so as to provide the maximum efficiency in serving the passenger service requirements.

  - Group Control Dispatching System

The dispatching system or group control system shall be de-centralised and the lifts shall not be dependent on a central control system for its effective group operation. Each lift control shall be capable of taking over the function of the group control.

  - Group Control Up Peak Mode

The Up Peak Mode shall be initiated automatically by recognising or anticipating traffic patterns or when a pre-determined number of cars with a loading above a predetermined weight level leave the main landing in the up direction.  Cars shall be permitted to depart from the main landing without predetermined timing.  During the Up Peak, down calls shall be served by cars not immediately needed to serve up traffic.

The Up Peak shall be discontinued once a predetermined number of cars with a loading below a predetermined level leave the main landing in the up direction. To suit individual building requirements, it shall be possible to alter the variables, which activate and de-activate the Up Peak without making changes to prints, hardware, the main program or fixed wiring.

  - Group Control Down Peak Mode

The Down Peak condition shall be detected by monitoring the number of down landing calls, down boarding rates and down lobby arrival loadings.  Under heavy Down Peak traffic, landing calls shall be grouped in sequence of registration and assigned to be served in this sequence in an approximate “first in / first out” pattern.  To suit individual building requirements, it shall be possible to alter the variables, which activate and de-activate the Down Peak without making changes to prints, hardware, the main program or fixed wiring.

  - Group Control Distribution of Free Cars

If no car call has been assigned after the lift has answered the last call, the car and landing doors shall close and the lift shall park at this landing awaiting a further assignment of a landing call or assignment to another zone or parking floor.  Cars having completed service shall be dispatched after a software adjustable time period to designated floors so that possible future calls shall not keep passengers waiting for long periods of time. The free cars shall not open their car doors when arriving at a parking floor and the doors shall remain closed until required to respond to an assigned call.  The distribution of free cars shall take into account additional main landings and priority floors in the following order of priority, unless otherwise specified:

- Main lobby:			Priority 1

- Additional main landings:	Priority 2

- Executive floors:		Priority 3

- Restaurant floors:		Priority 4

The main landing / lobby shall have the highest priority when distributing free cars.  If two or more free cars are parked on the main landing, only the available free car/master, shall park with its doors open.

  - Automatic Landing By-pass

When a car load exceeds a predetermined weight level, it shall automatically bypass all landing calls in the direction of service and shall respond only to car calls.  The default setting for this predetermined level shall be 65% of rated load.

  - Car Held Up at a Landing

Should a lift be delayed at a typical floor beyond a pre-set software adjustable time period initially set at thirty (30) seconds, the lift shall be disconnected from the group automatic operation and the assigned landing calls shall be re-assigned to an alternative operational lift.

  - Car Call Cancelling

When the car has responded to the last call in the up or down direction, the car calls shall automatically be cleared from the system to maintain optimum efficiency.

  - Load Weighing

Each lift shall be provided with a strain gauge load weighing device to ensure optimum service. This device shall be capable of constantly monitoring the load on the car platform with an accuracy of ± 5.0 kg.

  - Anti-nuisance Control

When a lift with a loading level of less than 20 kg arrives at a landing, all car calls shall be reset automatically.

  - Motor Generator Set Time-out

When a lift does not receive a group demand dispatch at the dispatching landing for a software adjustable time period up to 10 (ten) minutes, set initially at 5 (five) minutes, the motor generator set, if provided, shall stop and shut down the car lighting and ventilation automatically after it has opened the car and landing doors. If solid-state motion control is provided, timing devices shall be provided to accomplish this shutdown.

When a dispatch demand is received from the supervisory system by a lift whose generator is stopped, its motor generator shall automatically restart and re-energise the car lighting and ventilation circuits.

- Operation with Independent Service

- A two position key operated switch, with removable cylinder as approved by the Representative/Agent and master keyed to the building system, shall be mounted in the main car operating station of each lift specified for Independent Service Operation.  When this switch is in the on position, the removal of the key from the barrel shall be prevented and the lift shall be operated from the car buttons only and independent of all other automatic or special operation modes.

- The power operated car and lift shaft doors shall remain open when a lift is at a landing until a car call for another landing is registered and the door close button is pressed. If another car call has been registered, it shall be necessary, after each stop, to repress the door close button to affect the closing of the doors.

- It shall further be possible to activate and de-activate this service through the remote monitoring control station.

- Operation with Inspection

A two position switch shall be provided on top of the car enclosure to operate each lift manually during adjustment, inspection, maintenance and repair.  The operating buttons shall be of the continuous pressure type and the speed of the car shall not exceed 0.63 m/s.  It shall operate the car only when the car doors and all lift shaft doors are closed and all safety circuits made.

- Emergency Operation

A two position switch shall be provided in the motor room to operate each lift manually during emergency conditions, adjustment, inspection, maintenance and repair.  The operating buttons shall be of the continuous pressure type and the speed of the car shall not exceed 0.63 m/s.  Emergency operation shall operate the car only when the car doors and all lift shaft doors are closed and when the inspection control on top of the car is switched to normal operation.  However, it shall be permitted to override the final limits, safety contacts and governor contacts.

- Fireman’s Operation

  - Fire Recall – Level-1

- All lifts shall be equipped with Fire Control Level-1 and each group or single lift shall be equipped with a common Fire Control switch to recall the lifts (non-stop) to the nominated evacuation landing, where it shall remain parked with open doors. The switch shall be mounted in a box with a break-glass front marked "Lift Fire Control".

- When the switch is activated, cars travelling away from the designated landing, shall reverse at the next served floor without opening its doors, and return non-stop to the designated fireman's floor.

- An illuminated indicator fitted inside the car shall instruct the passengers to evacuate the lift at the designated evacuation floor.

- When on Standby Power the Fire Control operation shall operate as detailed under this section in conjunction with the Emergency Control sequenced evacuation shown under Section-3 Clause 7 (Operation with Standby Power) of this Specification.

  - Fire Recall – Level-2

- A Fire Service Key Switch mounted in the car operating panel shall be provided in each lift operating as a Fireman's Lift. Lifts operating as fireman’s lifts shall be as nominated by the Representative/Agent.

- A lift operating on Fire Service shall respond only to its own car call while ignoring all landing calls. When the lift arrives at a landing not being the main landing, its car and landing doors shall remain closed.  If the door open button is pressed, the doors shall open and continue opening.  If the door open button is released, the doors if not yet fully open, shall immediately reverse direction and close. Once the doors have been fully opened via the door open button, they shall remain open until a further car call has been registered and the door close button has been pressed.

- If more than one car call has been registered, all the remaining car calls shall be cancelled once the lift stops at the nearest car call in the direction of travel.

- If the lift remains stationary at a selected floor away from the main landing with the doors closed for an adjustable time initially set at 30 (thirty) seconds, the lift shall return to the fire recall floor automatically. When the lift returns to the main landing, the doors shall open automatically and remain open awaiting a further car call.

- All the car door horizontal and vertical light rays, ultrasonic and infrared detectives, shall be made inoperative during the firemen's service operation.

- It shall further be possible to initiate the fire control operation through the remote monitoring control station or fire detection system.  The Fire and Security Sub-Contractor shall provide a potential free contact in each lift motor room to indicate a fire condition.

- Operation wit Standby Power

  - Emergency Recall to Main Landing – Level-1

- Provide a standby power operation which recognises the feeder arrangement and the standby power operation which automatically evacuates all lifts on each affected feeder by operating 1 (one) lift at a time to the main dispatching landing without responding to car or landing calls.  The system shall subsequently permit automatic and manual selection of any lift to be released for normal operation with standby power.  If any lift fails to return to its main landing within 90 (ninety) seconds, it shall automatically be disconnected from the automatic return feature.

- The standby power supply shall be sized to run a predetermined number of lifts simultaneously.  The Electrical Sub-Contractor shall provide the number of lifts to run and the maximum kVA available for emergency operation. Alternatively, if this information is available it shall be as nominated by the Representative/Agent.

- In the event of a total failure of normal power, the feeder or feeders in each group shall be transferred to the standby power source.  A potential free normally closed contact shall be provided in the lift motor rooms to indicate the transfer to the standby power source. The potential free contact supplied by the Electrical Sub-Contractor shall open (fail to safety) when on standby power and the lifts will commence their sequenced evacuation.

- The lifts shall be capable of operation on standby power at minimum of 100% of rated speed in both directions and at a maximum load of 100% of rated capacity for a period of 10 (ten) minutes without overheating.

- All connections to the lift controls for standby power operation shall be provided in the appropriate machine rooms and all the necessary interlocking interconnection wiring among machine rooms shall be provided under this section.

  - Manual Release – Level-2

- Once all the lifts have been evacuated in sequence to the selected main landing, a predetermined lift or lifts shall be released for normal operation automatically or manually via a remote monitoring station.  All manual or automatic release shall be prevented until the automatic evacuation covered under Section-3 Clause 7.1 has taken place.

- The cars nominated / selected to run on emergency power shall not be fixed and it shall, furthermore, be possible to change the lift / lifts selected to run on emergency operation without making major changes to the lift wiring or control circuitry.

- In all instances the fireman’s lift shall have priority when selecting a lift or lifts to run on emergency power.

- Door Operation and Control

  - Independent Door Operation and Control

For lifts with two car entrances, the car doors front and back shall operate independently from its own car and landing call buttons, and associated door control equipment and this shall include the operation with independent service.

  - Car and Landing Doors for Access Goods Lifts Only

- The car and landing doors shall open and close quietly and smoothly. Doors shall be capable of being operated by hand.

- Each landing door shall be equipped with an electro-mechanical interlock so that the lift can only operate when the interlock circuit is established.

- Each car door/gate shall be equipped with a mechanical lock so that the lift can only operate when the car door is locked.

- An electric contact for the car door shall be provided that shall prevent the lift from moving away from a landing unless the door is in the fully closed position

- Overload Protection

Without exception, overload protection shall be provided (SABS1545-Part-1 1999 & EN81 Code 1997). When the load in the car enclosure exceeds the rated load, a buzzer shall sound, an overload indicator shall illuminate in the car operating panel and the lift doors shall remain open and the lift blocked from travelling. The overload device shall not be active during the travel.

- Drive Control

(a)	A fully regulated distance dependant closed loop VVVF, DC Ward Leonard, DC Direct Drive or Hydraulic drive control system shall be provided and shall constantly maintain the floor levels and ride quality as specified.  Lift acceleration, nominal speed and slowdown phases shall constantly be monitored and controlled against, and with reference to, distance, speed, current and voltage feedback loops.  The lift drive shall be capable of bringing the lift to a standstill after a travel without a “creeping in” or “levelling in” phase i.e. a direct approach.

(b)	Driving machine and motor shall be controlled to operate the lift continuously at 100% of rated speed in both directions without overheating or hunting during levelling.

- Ride Quality and Performance Criteria

  - Ride Quality Objective

The main objective is to be able to determine a ride standard and to maintain that standard by routine measurement and adjustment as necessary. The standards nominated are for lifts with rated speeds of 5 m/s or higher. Lower speed lifts should be able to perform better in terms of ride quality, and at worst the same parameters should be applied.

(a)	Vibration

Vibration, also sometimes referred to as “quaking”, is measured in three dimensions:

-	Lateral quaking from front to back.

-	Lateral quaking from side to side.

-	Vertical vibration (up and down).

The vibration levels are measured as acceleration levels of the car floor using an accelerometer. Measurements are expressed in terms of mm/s², milli-g or LAL. - 9.81 mm/s² = 1 milli-g or LAL.

Recording accelerometer tests in the horizontal plane shall be conducted prior to practical completion on each lift travelling at rated speed the full length of the shaft between terminal landings in both up and down directions with a maximum load of 230 kg located in the centre of the platform.  Recordings shall be taken on the platform in the plane of the car guide rails and perpendicular to the plane of the car guide rails.

One set of recordings for each lift shall become the property of the Employer as a permanent record. If these tests show that the equipment is in any way defective, at variance with the specified requirements, or objectionable in any operation, the Contractor shall make any change necessary to remedy these defects. All expenses for carrying out this remedial work and the costs of all subsequent tests including labour, material, test equipment, on site observations, etc, shall be for the Contractor's account.

Notice of all tests shall be given to the Representative/Agent in writing at least 96 hours prior to conducting the test.

(b)	Noise Levels

Noise levels in the car are measured during operation of the lift. Maximum and mean dB (A) figures are measured.

  - Performance Criteria

After practical completion the Contractor shall confirm that the lift equipment performs in accordance with the contract documents and shall provide documentation to substantiate accordingly.

The lifts shall be adjusted as required to, at least meet the following performance requirements within a 10% tolerance:

(a)	Ride quality

Acceleration / Deceleration:	max	1.0 m/s²

Jerk Rate:	max	2.0 m/s3

Stack changes:	nil

Shooting Off or Rollback:	nil

Car Noise:	max	56 dB (A)

Car Noise:	mean	52 dB (A)

(i)	Lateral Quaking ISO X & ISO Y (Velocity m/sec to Time / Drive Curve)

ISO Y = Side to side movement

ISO X = Front to back movement

Peak to peak:	max	15 milli-g

Peak to peak:	mean	5.0 milli-g

RMS:		mean	1.7 milli-g

(ii)	Vertical Vibration ISO-Z (Velocity m/sec to Time / Drive Curve)

Peak to peak:	max	10 milli-g

Peak to peak:	mean	3.0 milli-g

RMS:		mean	1.2 milli-g

(iii)	Vertical Vibration Start and Stop Kicks

Peak to peak:	max	18 milli-g

(b)	Levelling Tolerance

Re-levelling:		max.	3 mm

Levelling Accuracy:		max.	3 mm

(c)	Cycle Time

Times specified are for a typical floor-to-floor run of 3400 mm with a balanced load.

Door close to car start: 	max.	0.8 sec

| Rated Speed | to |  | Car Start Car Stop |
| --- | --- | --- | --- |
| >1.6 m/s |  | <5.0 sec. |  |
| 1.0 m/s |  | 5.6 sec. |  |
| 0.63 m/s |  | 10.5 sec. |  |

(d)	Door Dwell Times

| Passenger Conditions | Stops for Car Call | Landing Call |
| --- | --- | --- |
| First Passenger | 2.0 sec. | 3.0 sec. |
| Succeeding Passengers | 1.0 sec. | 1.0 sec. |

(e)	Door Open and Close Times

| ##### Door Opening | #### Type | ##### Door Open | ##### Door Closed |
| --- | --- | --- | --- |
| 900 mm | C/O | max. 2.2 sec | max. 3.0 sec |
| 1100 mm | C/O | max. 2.2 sec | max. 3.0 sec |
| 1200 mm | C/O | max. 2.4 sec | max. 3.2 sec |
| 1400 mm | C/O | max. 2.7 sec | max. 3.5 sec |

(f)	Door Pre-Opening

Max. 3/4 open when lift is within 5 mm of floor level.

SPECIFICATION FOR THE INSTALLATION OF

# LIFTS, ACCESS GOODS LIFTS ONLY AND ESCALATORS

SECTION 4 – DETAILED LIFT REQUIREMENTS

## TABLE OF CONTENTS

| Clause |  | Page |
| --- | --- | --- |
|  | General Requirements…………………………………………………………... | 4.1 |
|  | Description of Lift System……………………………………………………….. | 4.1 |
|  | Technical Requirements for Group-1.…………………………………………. | 4.2 |
|  | Technical Requirements for Group-2………………………………………….. | 4.4 |

### SECTION 4 – DETAILED LIFT REQUIREMENTS

- General Requirement

Tenderers shall offer lifts designed to comply with the technical requirements and the as described in Sections 2 and 3 of this specification.

The equipment offered shall be suitable for continuous operations under the following conditions:

- Electricity Supply

3-phase, 4-wire, 50HZ, AC with nominal voltage of 400/231V varying between 95% and 105% of the nominal voltage.

- Ambient Air Conditions

Max. Temperature		: ……….°C

Min. Temperature		: ……….°C

Max. relative humidity	: ……….%

- Altitude of site

……m above sea level

All equipment of the lift installation shall be Y2K compliant in all respects.

All lifts shall comply with the latest edition of SABS1545-1 and SABS-1545-2 specifications.

Copies of ISO9002 accreditation shall accompany the tenders submitted.

The lift installation shall comply in al respects with the requirements of the Occupational Health and Safety Act, Act 85 of 1993 as amended.

- Description of Lift System

| Description | Lift Number | Stops | Floors | Speed | Load | Units |
| --- | --- | --- | --- | --- | --- | --- |
| Group-1 North | L1, L2 & L3 | 5 | B, G, 1, 2 & 3 | 1.6 m/s | 1600-kg | 3 |
| Group-2 South | L1 & L2 | 4 | G, 1, 2 & 3 | 1.0 m/s | 1600-kg | 2 |
| Etc. |  |  |  |  |  |  |

- Technical Requirements for Group-1

  - General

| Item | Description | Detail Requirements |
| --- | --- | --- |
|  | Number of Units | 3 |
|  | Type of Lift | Passenger or Goods/Passenger or Goods Access Only |
|  | Load | 630 or 1000 or 1250 or 1600 or 2000 or 2500 kg |
|  | Speed | 0.63 or 1.0 or 1.6 m/s |
|  | Lift Numbers | L1, L2 & L3 |
|  | Total Travel | 30 |
|  | Number of Stops | 10 |
|  | No of Openings | 10 vertical in line |
|  | Car Entrances | One per Lift |
|  | Floor Designation | B, G, 1, … , 8 |
|  | Pit Depth | 1300 |
|  | Machine Room Dimension | 2200 x 3500 x 2100mm |
|  | Pit Service Platform | N/A |
|  | Extended Buffers | N/A |
|  | Access below Pit | N/A |
|  | Counterweight Safeties | N/A |

  - Machine

| Item | Description | Detail Requirements |
| --- | --- | --- |
|  | Drive | Traction, VVVF or Hydraulic |
|  | Machine | Geared |
|  | Roping | 1:1 or 2:1 |
|  | Automatic Self-Levelling | Yes, As Specified |
|  | Compensation | Yes, As Specified |

  - Control Operation

| Item | Description | Detail Requirements |
| --- | --- | --- |
|  | Operation | ## Group Automatic Operation |
|  | Up/Down Peaks | Yes, As Specified |
|  | Fire Control | Level-1, As Specified |
|  | Fireman’s Floor | Ground Level |
|  | Emergency Power Control | Level-1 & -2, As Specified |
|  | Evacuation Floor | Ground Level |
|  | Independent Control | Yes, As Specified |
|  | Load Measuring | Over Load, Landing Call By-pass, Anti-Nuisance |

  - Landing Equipment

| Item | Description | Detail Requirements |
| --- | --- | --- |
|  | Landing Doors Opening | 1100 x 2100mm Clear Opening, |
|  | Door Operation | Single Speed, Centre Opening |
|  | Door Control | VVVF Motion Control |
|  | Position Indicator | Digital Indicators on Main Landing (Ground Level) Only |
|  | Waiting Lanterns | Yes, As Specified |
|  | Gongs | Yes, As Specified |
|  | Call Buttons | Approved, Vandal Proof Mechanical Micro-Push Button |
|  | Direction Arrows | Yes, As Specified – Above all Landing Entrances |

  - Car Equipment

| Item | Description | Detail Requirements |
| --- | --- | --- |
|  | Number of COP’s | ## One per Lift |
|  | Protection Drapes | No |
|  | Position Indicators | Yes, As Specified on COP |
|  | Direction Arrows | Yes, As Specified on COP |
|  | Intercom | Yes, As Specified – Master Station - Security Control |
|  | Call Buttons | Approved, Vandal Proof Mechanical Micro-Push Button |
|  | Door Detectors | Yes, As Specified – Ultrasonic Proximity Detectors |
|  | Signage | Yes, As Specified |
|  | Emergency Light | Yes, As Specified |
|  | Braille Call Buttons | Yes, As Specified |

  - Shaft Dimensions and Equipment

| Item | Description | Detail Requirements |
| --- | --- | --- |
|  | Shaft Dimensions | 2200 x 2000mm |
|  | Head Room | 3800mm |
|  | Pit Sump | Supplied by Others |
|  | Shaft Lighting | Yes, As Specified |

  - Car Enclosure

| Item | Description | Detail Requirements |
| --- | --- | --- |
|  | Car Dimensions | 1600 x 1400 |
|  | Car Clear Internal Height | 2250 |
|  | Clear Door Opening | 800 x 2000mm |

  - Finishes

| Item | Description | Detail Requirements |
| --- | --- | --- |
|  | Fixture Faceplates | Minimum 3mm thick Stainless Steel (SST) with bevelled edges and a brushed finish |
|  | Car COP Faceplates | Full height next to car door SST with brushed Finish |
|  | Car Side Walls | SST – Brushed Finish |
|  | Car Rear Wall | SST – Brushed Finish |
|  | Car Front | SST – Brushed Finish |
|  | Car Floor | Normament – Principal Agent to Specify Colour |
|  | Car Ceiling | High Quality Suspended Ceiling with recessed Fluorescent Luminaires |
|  | Hand Rails | At a height of 900mm above car floor on sides and rear of car |
|  | Car Doors | SST – Brushed Finish |
|  | Landing Doors | SST – Brushed Finish |
|  | Landing Frames | SST – Brushed Finish |
|  | Landing Signals | Fitted above landing entrances |

- Group-2 Specifics

Same Procedure as for Group-1

SPECIFICATION FOR THE INSTALLATION OF

# LIFTS, ACCESS GOODS LIFTS ONLY AND ESCALATORS

SECTION 5 – SCHEDULE OF TECHNICAL INFORMATION

## TABLE OF CONTENTS

| Clause |  | Page |
| --- | --- | --- |
|  | General……………………………….…………………………………………... | 5.1 |
|  | Technical Information Schedule …………..…………………………………... | 5.1 |
|  | Deviations from Specification as Alternative Offer…...………………………. | 5.5 |

SECTION 5 – SCHEDULE OF TECHNICAL INFORMATION

1.	GENERAL

Tenderers are required to complete the following Schedule of Technical Information and shall in addition, under separate cover, give full particulars of the equipment and installations offered as well as detailed descriptions of the various methods of control and operation.

2.	TECHNICAL INFORMATION SCHEDULE

| Item | Description | Details |
| --- | --- | --- |
| 1. | Manufacturer's name |  |
| 2. | Country of origin |  |
| 3. | % South African manufacture |  |
| 4. | Performance |  |
| a) | Car speed in m/s |  |
| b) | Average round trip time |  |
| c) | Maximum carrying capacity of each lift car |  |
| d) | Average waiting time after registration of a landing call |  |
| 5. | Main Hoist Motor |  |
| a) | Maker's name |  |
| b) | Type |  |
| c) | Rated output (kW) |  |
| d) | Time rating (starts/hr) |  |
| e) | Manufacturing standard and safety codes |  |
| f) | Maximum speed (RPM) |  |
| g) | Rated voltage (Volts) |  |
| h) | Full load current (Amps) |  |
| i) | Starting current (Amps) |  |
| j) | Type of bearings |  |
| k) | Maximum line current with lift starting with full contract load (Amps) |  |
| 6. | Type of Brake |  |
| 7. | Gearing (If Applicable) |  |
| a) | Material of worm |  |
| b) | Material of worm-wheel |  |
| c) | Type of thrust bearings |  |
| d) | Ratio of gearing |  |
| e) | Type of worm-shaft bearings |  |
| f) | Worm above or below wheel |  |
| 8. | Drive |  |
| a) | Diameter of traction sheave (rope centres) |  |
| b) | Type of grooving used on traction sheave |  |
| c) | Type of bearing for sheave shaft |  |
| d) | Diameter of smallest deflector pulley used |  |
| e) | Type of grooves provided on deflector pulleys |  |
| f) | Type of bearings for deflector pulleys |  |
| g) | Means provided for absorption of vibration |  |
| 9. | Switch gear and Control System |  |
| a) | Make of main circuit breaker |  |
| b) | Rupturing capacity of main circuit breaker (kA) |  |
| c) | Type of control system |  |
| d) | Control voltage |  |
| e) | Make of contactors |  |
| f) | Make of control relays |  |
| g) | Contact materials used for auxiliary and main contacts of controller switch gear |  |
| h) | Type of selector |  |
| 10. | Car and Doors |  |
| a) | Mass of complete car with doors and operating gear (kg) |  |
| b) | Net inside dimensions(width x depth x height) in mm |  |
| c) | Thickness of material of car and landing doors |  |
| d) | Finish of car and landing doors |  |
| e) | Clear width and height of car and landing entrances |  |
| f) | Type of door drive mechanism offered |  |
| g) | Type of suspension used for car and landing doors |  |
| h) | Type of proximity detectors |  |
| (I) | For passengers approaching from landing |  |
| (II) | For passengers leaving lift car |  |
| i) | Type of material used for inside finishes of car (i.e. panels, ceiling trim) |  |
| j) | Thickness and type of floorboards and floor covering |  |
| k) | How is car and platform isolated from supporting structure? |  |
| l) | Are car panels treated externally for sound absorption? |  |
| m) | Door speed: |  |
| (I) | Normal (m/min) |  |
| (II) | On force closing (m/min) |  |
| 11. | Ropes |  |
| a) | Maker's name |  |
| b) | Diameter of ropes (mm) |  |
| c) | Number of main ropes |  |
| d) | Breaking load of each rope (kN) |  |
| e) | Maximum working load of each rope |  |
| f) | Factor of safety |  |
| g) | Tensile strength of steel used (MPa) |  |
| h) | Number of strands in rope |  |
| i) | Number of wires per strand |  |
| j) | Construction and lay of rope |  |
| k) | Type of rope fastening used |  |
| l) | System of roping (i.e. 2:1 or 1:1, single or double wrap) |  |
| 12. | Counterweight |  |
| a) | Total mass (kg) |  |
| b) | Percentage of live load counter balanced (%) |  |
| 13. | Guide Rails |  |
| a) | Type and section |  |
| b) | Mass per metre-length (kg) for: |  |
| (I) | Car |  |
| (II) | Counterweight |  |
| 14. | Roller Shoes |  |
| a) | Type |  |
| b) | Material of tyres for roller type guides |  |
| 15. | Buffers |  |
| a) | Type |  |
| b) | Length of stroke |  |
| c) | Reactions on pit floor when buffers are hit at 115% of contract speed whilst car is carrying contract load |  |
| (I) | Car buffers |  |
| (II) | Counterweight buffers |  |
| 16. | Safety Gear |  |
| a) | Type |  |
| b) | Type of governor |  |
| c) | Stopping distance at overspeed with: |  |
| (I) | Car empty (mm) |  |
| (II) | With contract load (mm) |  |
| d) | Percentage over-contract speed when governor trips safety (%) |  |
| e) | Percentage over-contract speed at which governor trips motor supply |  |
| f) | Is safety still effective if governor rope breaks after application of safety device? |  |
| 17. | Steelwork at Top of Shaft |  |
| a) | Number and type of sections used |  |
| b) | Reactions on structure must be submitted with tender by indicating position, magnitude and direction of all reactions on a drawing |  |
| 18. | Levelling |  |
| a) | Levelling speed (m/s) |  |
| b) | Levelling tolerance guaranteed (Maximum) (mm) |  |
| c) | Will car and landing doors be fully open when car reaches floor level? |  |
| d) | What is distance of levelling zone above and below floor level? |  |
| 19. | Selector Type |  |
| 20. | Deviations from Specification as an Alternative Offer: Does the equipment offered comply strictly with the specification (Yes/No) |  |

3.	Deviations from Specification as Alternative Offer

If answer to 20 above is NO, tenderers shall give full details of all deviations between the alternative offered and specified equipment hereunder:

........................................................................................................................................................

........................................................................................................................................................

........................................................................................................................................................

……………………………………………………………………………………………………………….

……………………………………………………………………………………………………………….

……………………………………………………………………………………………………………….

………………………………………………………………………………………………………………..

TENDERER'S NAME AND ADDRESS

..................................................

Signature of Tenderer's

...........................................................................			Authorised Signatory

...........................................................................

...........................................................................

TEL NO. ..........................		DATE : ..........................

SPECIFICATION FOR THE INSTALLATION OF

# LIFTS, ACCESS GOODS LIFTS ONLY AND ESCALATORS

SECTION 6 – SCHEDULE OF QUANTITIES

## TABLE OF CONTENTS

| Clause |  | Page |
| --- | --- | --- |
|  | Schedule 1 – Quantities for Group-1…………………………………………... | 6.1 |
|  | Schedule 2 – Quantities for Group-2…………………………………………... | 6.1 |
|  | Summary of Schedules of Quantities.…………………………………………. | 6.2 |

### SECTION 6 – SCHEDULE OF QUANTITIES

- Schedule 1 -  Quantities for Group-1

| #### ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | R | c |
| 1.1 | Supply and installation of Group-1 lifts as described in this specification, including all material, equipment, labour and transportation as well as the twelfth month guarantee period | No | 3 |  |  |  |
| 1.2 | Perform all required inspections and tests as required by the Occupational Health and Safety Act, No 85 of1993, and as described in SABS1545 and SABS1543, including the issuing of the required Certificates | No | 3 |  |  |  |
| 1.3 | Compilation of Operation and Maintenance Manuals | No | 1 |  |  |  |
|  | Total Carried to Summary |  |  | R |  |  |

- Schedule 2 -  Quantities for Group-2

| #### ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | R | c |
| 2.1 | Supply and installation of Group-2 lifts as described in this specification, including all material, equipment, labour and transportation as well as the twelfth month guarantee period | No | 3 |  |  |  |
| 2.2 | Perform all required inspections and tests as required by the Occupational Health and Safety Act, No 85 of1993, and as described in SABS1545 and SABS1543, including the issuing of the required Certificates | No | 3 |  |  |  |
| 2.3 | Compilation of Operation and Maintenance Manuals | No | 1 |  |  |  |
|  | Total Carried to Summary |  |  | R |  |  |

3.	Summary of Schedules of Quantities

| ##### Schedule |  | ##### Page No |  | ###### Amount |
| --- | --- | --- | --- | --- |
|  |  |  |  | R c |
| 1. | Quantities for Group-1……………… | 6.1 |  |  |
| 2. | Quantities for Group-2……………… | 6.1 |  |  |
| Total Tender Price Excluding VAT for Lift Installation |  |  | R |  |

*Note to Consultant (Note must no be included in document)

Consultant must ensure that all the items of the above schedules must be included in the bills of quantities.

SPECIFICATION FOR LIFT INSTALLATION

ADDITIONAL SPECIFICATION

OPERATING AND MAINTENANCE MANUALS

CONTENTS

1.	SCOPE

2.	PROCEDURE FOR SUBMISSION OF MANUALS

3.	FORMAT OF OPERATING AND MAINTENANCE MANUALS

4.	CONTENTS

1.	SCOPE

The Contractor shall be responsible for the compilation of complete sets of Operating and Maintenance Manuals.  A separate Operating and Maintenance Manual shall be supplied for each installation.

2.	PROCEDURE FOR SUBMISSION OF MANUALS

2.1	Submission Of Draft Manuals

A draft copy of each Operating and Maintenance Manual shall be submitted to the Representative/Agent prior to safety inspection of the installation.  Approval of the draft Operating and Maintenance Manuals shall be a prerequisite for commencement of the safety inspection in terms of the Occupational Health and Safety Act, 1993 (Act No. 85 of 1993)

The manuals will be reviewed and checked by the Representative/Agent and returned to the Contractor with comments, where necessary.  The Contractor shall make the necessary changes and amendments to the manuals to incorporate the Representative/Agent’s comments.

# 2.2	Development Of Final Manuals

A final draft copy of each Operating and Maintenance Manual shall be submitted to the Representative/Agent at least one week prior to commencement of Day 1 tests on commissioning.  This set of manuals will not be accepted without the Contractor’s verification of the information contained in the manuals and the professional language editing thereof.  The Representative/Agent shall return the manuals to the Contractor, who shall make the final corrections.  The Representative/Agent will, however, not be responsible for the quality control on manuals. Approval of final Operating and Maintenance Manuals shall be a prerequisite for issuing of a Certificate of Practical Completion for repair of the installation.

After the Representative/Agent has approved the final Operating and Maintenance Manuals, the Contractor shall provide the Representative/Agent with seven (7) sets of the manuals.  Approval of the final Operating and Maintenance Manuals shall be a prerequisite for issuing of a Certificate of Completion.

3.	FORMAT OF OPERATING AND MAINTENANCE MANUALS

(a)	Manuals shall be bound in hardcover lever-arch files with plastic coatings.  The files shall be clearly labelled on the front cover, as well as on the back band, with the following information:

(i)	The title "Operating and Maintenance Manuals"

(ii)	Name of the

(iii)	Name of the contract and contract number

(iv)	The Contractor’s name, address and contact telephone number and fax (logo optional)

(v)	Month and year in which the manuals are finally handed over to the Employer

- Name of the User Client.

(b)	Pamphlets and bound leaflets/booklets from suppliers or manufacturers shall be placed in plastic pockets.

(c)	Drawings and diagrams larger than A3 shall be folded and placed in plastic pockets to be easily removed or stored.

(d)	The sections of the manuals specified below shall be clearly partitioned.

(e)	Cross-referencing between drawings/diagrams and text shall be in a clear and consequent format.

(f)	The Operating and Maintenance Manuals shall be supplied in English.

4.	CONTENTS

4.1	Table Of Contents

The table of contents shall appear on the second page and shall consist of the headings of the various sections in the manual and the relevant page numbers.

The table of contents shall essentially contain at least the following:

1.	Introduction

1.1	Scope of the manual

1.2	General arrangement of the manual

1.3	Description of installation

1.4	Specifications

2.	List of drawings and diagrams

3.	Parts and components

4.	Operating procedures

5.	Maintenance

5.1	Purpose of maintenance

5.2	Preventative maintenance

5.3	Trouble-shooting

6.	Breakdown maintenance and repair

7.	List of Appendices.

4.2	Introduction

The introduction shall contain at least the following:

# 4.2.1	Scope of the manual

A summary shall explain the scope of the contents.

4.2.2	General arrangement of the manual

A brief description shall explain the way in which the manual is arranged.

## 4.2.3	Description of installation

This section shall give a functional description of the complete installation covered by the manual, including all systems and/or functional units deemed to form part thereof.

## 4.2.4	Specifications

A summary shall be given of the specifications applicable to the particular part of the Contract.

4.3	Drawings And Diagrams

4.3.1	Mechanical flow diagrams (MFDs) and single line diagrams

Mechanical flow diagrams (for mechanical systems) or single line diagrams (for electrical systems) of the system and/or functional unit shall be included in the Operating and Maintenance Manuals for easy reference by the operators of the installation.  Diagrams shall be drawn not only for parts of an installation that have been repaired, but also for the complete installation, including all the components.

4.4	Parts And Components

#### 4.4.1	Equipment data sheets

A data sheet shall be drawn up for each piece of equipment and/or machine forming part of the installation and shall contain the following information:

(a)	Equipment tag number

(b)	Equipment description

(c)	Model/make/manufacturer

(d)	Supplier/Reconditioning details

(e)	Ordering details

(f)	Details of fixed components

(g)	Details of lubrication

(h)	Maintenance references (refer to supplier/reconditioning technical manual).

4.4.2	Technical equipment manuals

For each piece of equipment and/or machine forming part of the installation the following information shall be included in this section of the Operating and Maintenance Manuals:

(a)	The supplier or reconditioning manual and/or standards of operating and maintenance instructions;

(b)	illustrated parts breakdown and/or group assembly drawings as agreed with the Representative/Agent;

(c)	parts lists and data sheets, including all characteristic curves for machines indicating operation point, efficiency, power consumption, etc;

(d)	calibration charts, and

(e)	test certificates for hydraulic pressure tests, flame-proof grading, materials, non-destructive examinations, coating and lining details, etc.

Each detailed description shall be accompanied by a set of engineering drawings. From the drawings the functionality of each part or component used, as well as the special characteristics associated with the part or component shall be very clear.

# 4.4.3	Parts and components list

A detailed description shall specify all the parts and components used for the duration of the Contract.  This description shall include new parts and components, as well as existing parts and components that have either been reconditioned or used as specified in the Contract.

The description shall state at least the part or component number, part or component name, the size of the part or component, an explanatory description, the quantity used, the material of which the part or component is made,  the coating (if any), date of purchase, as well as any relevant remarks as to the application thereof.

Details of the manufacturer of the part or component shall also be listed.  This shall at least state the name, address, telephone number, fax number and name of a contact person.

The supplier of the part or component shall also be stated and shall include at least the name, address, telephone number, fax number, name of a contact person and an alternative supplier (if available).

4.4.4	Drawings

Drawings shall contain a descriptive heading, an explanatory key and relevant comments.  Drawings shall be done on a computer-aided design package approved by the Representative/Agent.

A compound drawing for all subassemblies shall clearly indicate how and where the various parts fit in the subassembly.  The compound drawing shall be linked to the equipment data sheets and parts and components list and shall clearly specify the parts or components used, their model numbers, their sizes and the quantities used.  The compound drawings shall also be accompanied by a short description explaining the workings of the subassembly, as well as the assembly of the parts or components to complete the subassembly.

4.5	Operating Procedures

The operating instructions shall be a step by step description of the manual start-up and shut-down procedure for every piece of equipment and/or process reconditioned, repaired or supplied with references to the MFDs.  For automatic operation the operators shall be referred to the automatic control manual (if applicable).

The functioning of the installation shall be clearly described, using a flow diagram depicting the interrelationships among the various subassemblies.  The subassemblies shall be described by descriptive drawings.

Each mechanical or process flow diagram shall contain at least a heading, relevant comments and a key.

Every subassembly shall also have its own flow diagram explaining the operation of the subassembly, as well as the application of each part and component.  The application of the subassembly shall also be very clear.  The flow diagram shall consist of at least a heading, relevant comments and an explanatory key.

A detailed description shall be given of all operational systems forming part of the installation, explaining the operation and functioning of the system and the number of operations personnel required for performing the operation successfully.

The preparations, which are required before the system can be operational, shall be clearly stated and explained.

The operation tasks shall be clearly explained with reference to dangerous situations that might occur.  Hazardous operations shall be explained in great detail and cover all the applicable safety precautions.

4.6	Maintenance

4.6.1	Purpose of maintenance

The maintenance process shall be explained and the main responsibilities described.

4.6.2	Preventative maintenance

A preventative maintenance and lubrication schedule shall be included in this section.  This schedule shall be in table format and shall include a summary of all the maintenance actions required for each different system and/or functional unit covered by this manual, in order to give a single summary of all routine preventative maintenance actions required for the complete installation.

The schedule shall indicate daily, weekly, fortnightly, monthly and yearly maintenance actions.  A lubrication schedule summary shall also be included under this section.

The frequency of routine preventative maintenance actions shall be indicated very clearly.

The Contractor shall provide the maintenance requirements as prescribed by the manufacturer.  The type of maintenance shall be clearly indicated.  The description of the maintenance to be performed shall include at least the part name, location of the part in either the assembly or subassembly, the model number, the quantity of the particular part or component to be maintained, the type of maintenance, and notes on the maintenance procedure.

A brief description shall accompany the maintenance schedule, indicating special tools to be used, maintenance and test equipment required for the test procedures.  Any special tools necessary for maintenance shall be specified in terms of name, model, size, manufacturer, supplier (name, telephone number, fax number, contact person), coating (if any) and notes on the use of the equipment.

Remarks on the system readiness checks of each subassembly shall be explained in detail.  Routine inspection and maintenance processes shall be described.  It shall be very clear what needs to be done, how to perform the necessary task and any dangers that are present.

##### 4.6.3 Trouble-shooting

An explanation shall be given to assist the maintenance personnel in analysing and resolving malfunctions that might occur.  Various scenarios with possible causes and rectification procedures shall be explained.

The scenarios shall be accompanied by drawings indicating the position of the part that is faulty.  Each of these drawings shall have a heading, comments and an explanatory key.

##### 4.7	Breakdown Maintenance And Repair

The Contractor shall describe the complete procedure to be followed in the event of a breakdown.  It shall be very clear what the operating personnel should look for, how to eliminate any dangers due to the breakdown (e.g. electricity must be shut off in the event of problems with the wiring) and who should be contacted.  The Contractor shall supply the names and telephone numbers of at least two contact persons who may be contacted in the event of a breakdown.

Repair instructions shall provide the maintenance personnel with detailed instructions for the removal and/or replacement of any item requiring replacement due to malfunctioning.  Contact numbers shall also be given to assist maintenance personnel, should a breakdown occur.

The Contractor shall specify the actions expected of maintenance personnel in the event of a breakdown.

The Contractor shall also specify the testing procedures to be followed before the system can be put into operation again.  Every procedure shall be described clearly and all the potential dangers pointed out, as well as the precautions that have to be taken.

The testing procedures shall be accompanied by drawings illustrating the process to be performed.  Every drawing shall have a heading, comments and an explanatory key.

# ANNEXURE A

## SCHEDULE OF IMPORTED MATERIALS AND EQUIPMENT

## TO BE COMPLETED BY TENDERER

The Contractor shall list imported items, materials and/or equipment which shall be excluded from the Contact Price Adjustment Provisions and shall be adjusted in terms of currency fluctuations only. Copies of the supplier’s quotations for the items, materials or equipment (not higher than the Contract rate as listed below) should be lodged with the Representative/Agent of the Department of Public works within 60 (sixty) days from the date of acceptance of the tenders. No adjustment of the contractor’s profit, local VAT amount, discount, mark-up, handling costs, etc. shall be allowed.

| ITEMS | MATERIAL / EQUIPMENT | RAND (R) EXCLUDING VAT |
| --- | --- | --- |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |
| 6 |  |  |

FORMULA:

The net amount to be added to or deducted from the contract sum:

A	=	V	x	Z

Y

A	=	the amount (R) of adjustment

V	=	the net amount (R) (Supplier’s Quotation) of the imported item

(Material or Equipment)

Y	=	exchange rate at the closing date of tender submission

Z	=	exchange rate on the date of payment

PW 379 M (Hans)