## Cover
DEPARTMENT OF PUBLIC WORKS AND INFRASTRUCTURE
Comprising of:
Section 1 - Preliminaries and General
Section 2 - Generator Installation
Section 3 - LT Distribution and Service Reticulation
Section 4 - Electrical Installation
Section 5 - Prime Cost Sum
Section 6 - Summary

## Section 1
MARION ISLAND GENERATOR UPGRADE AND ELECTRICAL INSTALLATION
ELECTRICAL ENGINEERING SERVICES
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PART 1A: PRELIMINARY AND GENERAL
The agreement is to be the General Conditions of
Contract (GCC 2010) (Second Edition), Published by the
SA Institution of Civil Engineering.
The preliminaries are to be the Construction and
management requirements for works contracts - Part 1:
General engineering and construction works (SANS 1921
-1: 2004 Edition 1) prepared by Standards South Africa
and shall be deemed to be incorporated herein.
Tenderers are referred to the abovementioned
documents for the full intent and meaning of each clause
thereof (hereinafter referred to by heading and clause
number only) for which such allowance must be made
as may be considered necessary.
Where standard clauses or alternatives are not entirely
applicable to this contract such modifications,
corrections or supplements as will apply are given under
each relevant clause heading.
Where any item is not relevant to this specific contract
such items is marked N/A (signifying "not applicable").
Adjustment of the preliminaries: each item priced, is to
be allocated to one or more of the three categories,
where "F" denotes a fixed amount (amount not to be
varied), "V" denotes an amount variable in proportion to
value and "T" denotes an amount in proportion to time.
Time (T) related Preliminaries will only be adjusted for
omissions or additions, issued by the Employer, or
delays caused by the Employer, for which variation and
extention of time has been granted.
SECTION A: GENERAL CONDITIONS OF CONTRACT
A1 | General (Clause 1)
| F: …………... V: ………….. T: …………… | Item | 1
A2 | Basis of Contract (Clause 2)
| F: …………... V: ………….. T: …………… | Item | 1
A3 | Engineer (Clause 3)
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
A4 | Contractor's General Obligation (Clause 4)
| F: …………... V: ………….. T: …………… | Item | 1
A5 | Time and Related Matters (Clause 5)
| F: …………... V: ………….. T: …………… | Item | 1
A6 | Payment and Related Matters (Clause 6)
| F: …………... V: ………….. T: …………… | Item | 1
A7 | Quality and Related Matters (Clause 7)
| F: …………... V: ………….. T: …………… | Item | 1
A8 | Risk and Related Matters (Clause 8)
| F: …………... V: ………….. T: …………… | Item | 1
A9 | Termination of Contract (Clause 9)
| F: …………... V: ………….. T: …………… | Item | 1
A10 | Claims and Disputes (Clause 10)
| F: …………... V: ………….. T: …………… | Item | 1
SECTION B: SANS 1921-1:2004 (Edition 1):
CONSTRUCTION AND MANAGEMENT
REQUIREMENTS FOR WORKS CONTRACTS: PART 1
B1 | Scope
| F: …………... V: ………….. T: …………… | Item | 1
B2 | Normative references
| F: …………... V: ………….. T: …………… | Item | 1
B3 | Definitions
| F: …………... V: ………….. T: …………… | Item | 1
B4 | Requirements for construction and management
| F: …………... V: ………….. T: …………… | Item | 1
B4.1 | General
| F: …………... V: ………….. T: …………… | Item | 1
B4.2 | Responsibilities for design and construction
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
B4.3 | Planning, programme and method statements
| F: …………... V: ………….. T: …………… | Item | 1
B4.4 | Quality assurance
| F: …………... V: ………….. T: …………… | Item | 1
B4.5 | Settling out
| F: …………... V: ………….. T: …………… | Item | 1
B4.6 | Management and disposal of water
| F: …………... V: ………….. T: …………… | Item | 1
B4.7 | Blasting
| F: …………... V: ………….. T: …………… | Item | 1
B4.8 | Works adjacent to services and structures
| F: …………... V: ………….. T: …………… | Item | 1
B4.9 | Management of the works and site
| F: …………... V: ………….. T: …………… | Item | 1
B4.10 | Earthworks
| F: …………... V: ………….. T: …………… | Item | 1
B4.11 | Testing
| F: …………... V: ………….. T: …………… | Item | 1
B4.12 | Materials, samples and fabrication drawings
| F: …………... V: ………….. T: …………… | Item | 1
B4.13 | Equipment
| F: …………... V: ………….. T: …………… | Item | 1
B4.14 | Site establishment
| F: …………... V: ………….. T: …………… | Item | 1
B4.15 | Survey control
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
B4.16 | Temporary works
| F: …………... V: ………….. T: …………… | Item | 1
B4.17 | Existing services
| F: …………... V: ………….. T: …………… | Item | 1
B4.18 | Health and safety
| F: …………... V: ………….. T: …………… | Item | 1
B4.19 | Environmental requirements
| F: …………... V: ………….. T: …………… | Item | 1
B4.20 | Alterations, additions, extentions and modifications to
existing works
| F: …………... V: ………….. T: …………… | Item | 1
B4.21 | Inspection of adjoining structures, services, buildings
and property.
| F: …………... V: ………….. T: …………… | Item | 1
B4.22 | Attendance on nominated and selected subcontractors
| F: …………... V: ………….. T: …………… | Item | 1 |  | N/A
SECTION C: SCOPE OF WORK IN ACCORDANCE
WITH SANS 10403
(The reference to clauses refer to table B.1 of SANS
1921-1:2004)
C1 | Cerification by recognised bodies - (Clause 4.4)
| F: …………... V: ………….. T: …………… | Item | 1
C2 | Agrèment - (Clause 4.5)
| F: …………... V: ………….. T: …………… | Item | 1
C3 | Other services and facilities - (Clause 4.8)
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
C4 | Recording of weather - (Clause 5.2)
| F: …………... V: ………….. T: …………… | Item | 1
C5 | Management meetings - (Clause 5.3)
| F: …………... V: ………….. T: …………… | Item | 1
C6 | Daily records - (Clause 5.6)
| F: …………... V: ………….. T: …………… | Item | 1
C7 | Permits - (Clause 5.9)
| F: …………... V: ………….. T: …………… | Item | 1
C8 | Proof of compliance with the law - (Clause 5.10)
| F: …………... V: ………….. T: …………… | Item | 1
SECTION D: SPECIFICATION DATA ASSOCIATED
WITH SANS 1921-1:2004 (Table A.1)
D1 | Requirements for drawings, information and calculations
for which the contractor is responsible - (Clause 4.1.7)
| F: …………... V: ………….. T: …………… | Item | 1
D2 | The planning, programme and method statements-
(Clause 4.3)
| F: …………... V: ………….. T: …………… | Item | 1
D3 | Samples of materials. Workmanships and finishes -
(Clause 4.12.1)
| F: …………... V: ………….. T: …………… | Item | 1
D4 | Fabrication drawings that the contractor is to provide
and deliver to the employer - (Clause 4.12.2)
| F: …………... V: ………….. T: …………… | Item | 1
D5 | Office for the foreman - (Clause 4.14.3)
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
D6 | Telephone - (Clause 4.14.3)
| F: …………... V: ………….. T: …………… | Item | 1
D7 | Office for inspector of works - (Clause 4.14.3)
| F: …………... V: ………….. T: …………… | Item | 1 |  | N/A
D8 | Telephone in office for inspector of works -
(Clause 4.14.3)
| F: …………... V: ………….. T: …………… | Item | 1 |  | N/A
D9 | Provision and erection of signboards - (Clause 4.14.6)
| F: …………... V: ………….. T: …………… | Item | 1 |  | N/A
D10 | Termination, diversion or maintenance of existing
services - (Clause 4.17.1)
| F: …………... V: ………….. T: …………… | Item | 1
D11 | Services which are known to exist - (Clause 4.17.3)
| F: …………... V: ………….. T: …………… | Item | 1
D12 | Detection apparatus - (Clause 4.17.4)
| F: …………... V: ………….. T: …………… | Item | 1
D13 | Additional health and safety requirements -
(Clause 4.18)
| F: …………... V: ………….. T: …………… | Item | 1
SECTION E: SPECIFIC PRELIMINARIES
(Section E contains specific preliminaries items which
apply to this contract except where "N/A" (Not applicable)
appears against the item.
E1 | WORKING OVER THE WEEKEND
Contractor to make allowance to work over the
weekend in order to allow for the disconnection of
utilities and the connection of the generator. The
weekend to be used for disconnection and connection
and must be communicated to the Department two
weeks in advance.
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E2 | SITE INSTRUCTIONS
Site instructions issued on site are to be recorded in
triplicate in a Site Instruction book which is to be m
maintained on site by the Contractor
| F: …………... V: ………….. T: …………… | Item | 1
E3 | PLANT RECORD
At every site meeting, the Contractor shall provide the
Engineer/Principal agent with a written record, in
schedule form, reflecting the number, type and capacity
of all plant, excluding hand tools, currently used on the
works.
| F: …………... V: ………….. T: …………… | Item | 1
E4 | SITE OFFICE
The Contractor is to allow for the provision and removal
of a site office in accordance with the Principal Agent's
requirements. To accommodate 6 persons.
| F: …………... V: ………….. T: …………… | Item | 1
E5 | TRADE NAMES
Wherever a Trade Name for any product has been
described in the Bill of Quantities, the Bidder's attention
is drawn to the fact that any other product of equal quality
may be used, subject to the written approval of the
Principal Agent being obtained prior to the closing date
for the submission of the Bids.
| F: …………... V: ………….. T: …………… | Item | 1
E6 | INACCURATE AND DEFECTIVE WORK EXECUTED
UNDER PREVIOUS CONTRACT
The contractor shall, after taking possession of the site
and before commencing the work, check all levels, liners,
profiles and the like and satisfy himself as to the
dimensional accuracy of all work executed under the
previous contract which may affect his work.
Should any inaccurate or detecfive work be found, the
contractor shall immediately notify the principal agent
in writing requesting his instructions with regard thereto
and afford every facility to those rectifying such
inaccurate or defective work.
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E7 | VIEWING THE SITE IN SECURITY AREAS
If the site is situated in a security area and the bidder
must arrange with the Authorities to obtain permission
to enter the site for Bidding purposes.
| F: …………... V: ………….. T: …………… | Item | 1
E8 | COMMENCEMENT OF WORKS IN SECURITY AREAS
If the works falls within a security area, the contractor
must arrange with the Authorities and give the
necessary notices before commencement of the works.
Should the contractor fail to make such arrangements,
admission to the site may be refused and any aditional
costs will be for the contractor's account.
| F: …………... V: ………….. T: …………… | Item | 1
E9 | ENTRANCE PERMITS TO SECURITY AREAS
If the works falls within a security area, the contractor
shall obtain entrance permits for his personnel and
workmen entering the area and shall comply with all
regulations ans instructions which be issued from the
time to time regarding the protection of persons and
property under the control of the Authority.
| F: …………... V: ………….. T: …………… | Item | 1
E10 | PROHIBITION ON TAKING PHOTOGRAPHS
In terms of article 119 of the Defence Act, 44 of 1957,
it is prohibited to sketch or to take photographs of any
military site or installation or any building or civil works
thereon or to be in possession of a camera or other
apparatus used for taking photographs, except when
authorised thereto by or on behalf of the Minister
The same prohibition is also applicable to all
Correctional Institutions in terms of article 44.1 of the
Correctional Services Act 8 of 1959.
| F: …………... V: ………….. T: …………… | Item | 1
E11 | TOILET FACILITIES
Allow for the supply and removal of portable toilet
facilities. The contractor is to maintain the cleanliness
of the facilities throughout the contract period. The
contractor must provide enough toilets for his/her entire
workforce.
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E12 | MANAGEMENT OF WATER
Water for Construction puposes must be obtained from
alternative water sources (i.e. supply other than water
that is produced and distributed by a regulated water
service authority from a licensed water treatment works
for human consumption), e.g. dams, rivers, boreholes,
springs, rainwater harvesting, recycled sewerage water,
etc. The alternative water source shall not be of an
inferior quality/ standard than that required for
construction purposes. The client reserves the right
through his agents to test such supplies or request
certificates confirming the grade and nature of the water
supply. Relevant knowledge of the respective area will
be an advantage.
| F: …………... V: ………….. T: …………… | Item | 1
E13 | OCCUPATIONAL HEALTH AND SAFETY ACT &
CONSTRUCTION REGULATIONS
It is required of the Contractor to thoroughly study the
Health and Safety specification that must be read
together with and is deemed to be incorporated under
this section of the Bill of Quantities. Provision for pricing
thereof is made under items E12.1 to E12.15 hereafter
and it is explicity pointed out that all requirements of the
aforementioned specification are deemed to be priced
hereunder, as the said items represent the only method
of measurement and no additional items or extras to the
contract in this regard shall be entertained.
The contractor must take note that compliance with the
Occupational Health and Safety Act, Construction
Regulations and Health and Safety specification is
compulsory. In the event of partial or total non-
compliance, the Principal Agent , notwithstanding the
provisions of Clause 6 of Section 1: Preliminaries
(Part A) or any other clause to the contrary, reserves
the right to delay issuing any progress payment
certificate until the Contractor provides satisfactory
proof of compliance. The Contractor shall not be entitled
to any compensation of whatsoever nature, including
interest, due to such delay of payment.
All references hereafter are to Regulations of the
Construction Regulations, 2003 issued under the
Occupational Health and Safety Act, 1993 (Act No 85 of
1993).
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
The contractor shall, in submitting his bid, demonstrate
that he has made provision for the cost of compliance
with the specified health and safety requirements, the Act
and the Construction Regulations.
| F: …………... V: ………….. T: …………… | Item | 1
E13.1 | NOTIFICATION OF CONSTRUCTION WORK
(Construction Regulations 3)
The contractor shall, before commencing work, notify the
Department of Labour of the intend construction work in
terms o Regulation 3. The Contractor shall submit the
notification in writing, on the appropriate form, prior to
commencement of work.
| F: …………... V: ………….. T: …………… | Item | 1
E13.2 | HEALTH AND SAFETY PLAN (Construction
regulations 5.4)
The Contractor shall provide and demonstrate to the
Principal Agent a suitable and sufficiently documented
health and safety plan based on the Act, Construction
Regulations and the health and safety specification,
which shall be applied from the date of commencement
of and for the duration of the construction work. The
Contractor shall ensure that a copy of the health and
safety plan is available on request to an employee,
inspector, sub contractor or principal agent all in terms
of Regulation 5.
| F: …………... V: ………….. T: …………… | Item | 1
E13.3 | REGISTRATION WITH THE COMPENSATION FUND
(Construction Regulations 5.3 f)
The Contractor shall provide proof of his registration and
good standing with the Compensation Fund or a licensed
compensation insurer prior to the commencement of
work
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E13.4 | HEALTH AND SAFETY FILE ( Construction
Regulation 5.7)
The contractor shall ensure that a health and safety file,
which shall include all documentation required in terms
of health ans safety specification, the Act and the
Construction Regulations, is opened and kept on site
and made available to the Principal Agent or inspector
upon request. Upon completion of the works, the
contractor shall hand over a consolidated health and
safety file to the principal agent.
| F: …………... V: ………….. T: …………… | Item | 1
E13.5 | SUPERVISION OF CONSTRUCTION WORK ( Safety
officier) (Construction Regulation 6)
The Contractor shall appoint a full-time competent
employee in writing as the construction supervisor, with
the duty of supervising the construction work.
The Contractor shall appoint a full-time or part-time
construction safety officier in writing to assist in the
control of all safety related aspects on the site. Such
appointments are required to ensure that at all times the
requirements of the Act and Construction Regulations
are adhered to. Refer to Regulation 6.
| F: …………... V: ………….. T: …………… | Item | 1
E13.6 | RISK ASSESSMENT AND SAFETY POLICY
( Construction Regulation 7)
Before commencing work the Contractor shall cause a
risk assessment to be performed by a competent person
appointed in writing and the risk assessment shall form
part of the health and safety plan. A copy of the risk
assessment shall be available on site at all times for
inspection.
The Contractor shall at all time carry out the works in a
manner to avoid the risk of bodily harm to persons or
risk of damage to any property. He shall take all
precuations regarding training of employees in any
hazards and the related work procedures, health and
safety induction training of employees, visitors or any
other persons entering the site and provide personal
protective equipment to all employees and visitors to
site which are necessary and adequate to eliminate any
conditions which contribute to the risk of injury to
persons or damage to property in terms of Regulation 7.
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E13.7 | SIGNIFICANT HAZARD IDENTIFICATION RISK
ASSESSMENT PREPARED BY THE DESIGN
CONSULTANTS
The Contractor shall allow for additional finanical
provision, if any , to take the necessary precauations
regarding the significant hazards and risks identified
and assessed by the design consultants.
| F: …………... V: ………….. T: …………… | Item | 1 |  | N/A
E13.8 | ADDITIONAL FINANICAL PROVISION
The Contractor shall allow for additional finanicial
provision, if any, to comply with the requirements of the
Occupational Health and Safety Act ( Act No 85 of 1993)
and the Construction Regulations issued there under
which have not been specifically elsewhere.
| F: …………... V: ………….. T: …………… | Item | 1
E13.9 | FALL PROTECTION PLAN (Construction Regulation
8)
The Contractor shall, before commencing any
construction work submit a fall protection plan identified
all steps to be taken in order to ensure the continued
adherence to the fall protection plan and shall include
a risk assessment of all work carried out from a relevant
position. The fall protection plan shall form part of the
health and safety plan and file.
| F: …………... V: ………….. T: …………… | Item | 1
E13.10 | PHYSICAL AND PSYCHOLOGICAL FITNESS
(Construction Regulation 8.2 (b))
The Contractor and sub-contractor shall before
commencing any construction work submit proof of his
employees that shall carried out work from an elevated
position their physical and psychological fitness and
shall be recorded in the health and safety file.
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E13.11 | CONSTRUCTION VEHICLES AND MOBILE PLANT
(Construction Regulations 21)
The Contractor and sub-contractors shall ensure that all
operated workers received training and been certified
competent to operate such vehicles, and are physical
and psychological fit to operate such construction
vehicles and mobile plants and shall be recorded in the
health and safety file.
| F: …………... V: ………….. T: …………… | Item | 1
E13.12 | TRAINING (Construction Regulation 8 (c))
The Contractor and sub-contractor shall, before
commencing any construction work, submit his training
program of all his employees. This program shall form
part of the health and safety plan.
| F: …………... V: ………….. T: …………… | Item | 1
E13.13 | DEMOLITION WORK (Construction Regulations 12)
The Contractor shall, before any demolition work shall
be carried out, submit all methods of demolition to be
used. This method shall form part of the health and
safety plan and file.
| F: …………... V: ………….. T: …………… | Item | 1
E13.14 | REMOVAL AND DISPOSAL OF ASBESTOS
MATERIAL (Asbestos Regulation)
The principle contractor shall appoint a contractor that
is registered with the Department of Labour as an AIA.
The contractor must allow for:
NOTIFICATION OF ASBESTOS PROCESSING
PERSONAL PROTECTIVE EQUIPMENT
PACKAGING AND TRANSPORT AND STORAGE TO
DISPOSAL SITE
DEMOLITION WORK
LABELLING, INFORMATION, ETC.
| F: …………... V: ………….. T: …………… | Item | 1 |  | N/A
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E13.15 | RISK COMPLIANCE AREAS (As Outlined
In "Volume Three": Covid-19 Guidelines for
Management of Risk on Construction Sites and
Covid-19 addendum (Item 1-12) attached to
Health and Safety specification)
· Disinfection of the workplace at regular intervals as
outlined within the Guidelines "Annexure A"
Workplace Preparation Procedure;
· Ensure Staff and Security Staff have PPEs (i.e.
masks,gloves, sanitisers, etc.)
· Installed thermal scanners to check temperature of
all staff and visitors. Ensure training of Security Staff
for use of thermal scanners. Register to be
implemented for staff and visitors to site with
identification criteria "ID number, Name, Age,
Health Status and Contact details";
· Isolation room identified/constructed on site;
· Ensure sanitisers and soap are available in locker
rooms for staff;
· Ensure staff or visitors are wearing masks before
entering;
· Ensure social distance on site;
· Notification about the restriction of the number of
people allowed on site at one time;
· Disinfection of rooms for meetings and strictly
keeping to social distancing and wearing masks;
· Plans to rotate work force on percentage allowable
on site to comply with regulations;
· Permits issued by Authorising Authority for Work
Force and vehicles for Cross Provincial and District
Boarders
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E14 | IMPLEMENTATION OF LABOUR-INTENSIVE
INFRASTRUCTURE PROJECTS UNDER THE
EXPANDED PUBLIC WORKS PROGRAMME (EPWP)
The contractor shall comply with all the requirements of
the "Code of Good Practice for Employment and
Conditions of Work for Special Public Works
Programmes" issued in terms of the "Basic Conditions
of Employment Act, 1997 (Act No 75 of 1997)" and the
related "Ministerial Determination", for the employment
of locally employed temporary workers on a labour
intensive infrastructure project under the Expanded
Public Works Programme (EPWP)
The contractor shall maintain daily records with regard
to the workers employed and shall, on a monthly basis,
submit a report (Contract, ID Copy, Attendance register,
Proof of payment) to the principal agent in the
prescribed format. Compulsory indicators such as the
project budget, actual project expenditure, number of job
opportunities created, demographic characteristics of
workers employed, minimum daily wage rate, number of
person-days of employment created and number of
training person-days, shall be included in said report, all
as defined in the "Guidelines for the Implementation of
Labour-Intensive Infrastructure Projects under the
Expanded Public Works Programme (EPWP)"
Provision for pricing of compliance with the
aforementioned is made under this clause and it is
explicitly pointed out that all that all requirements in
respect of the aforementioned are deemed to be priced
hereunder and no additional claims in this regard shall
be entertained
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E14.1 | DECLARATION - EPWP PROGRAMME
The contractor must adhere to all rules, regulations and
requirements regarding the EPWP programme,
specifically but not limited to the following:
1. Labour intensive construction methods (LIC)
1.1 Comply to implementation of LIC BOQ items
specified elsewhere in the tender documents
2. Recruitment and placement of EPWP NYS (Not
Applicable)
2.1 Recruitment, placement and exposure training of
25 (Twenty five) participants
2.2 Comply to EPWP BOQ specifications and code of
good practice
3. Recruitment and placement of local labourers
3.1 Recruitment and placement of minimum 5 (Five)
local labourers
3.2 Comply with applicable wage order/determination
or agreement, in terms of labour relations act or
wage act
4. Comply with EPWP monthly reporting
requirements
Monthly prepare and submit below EPWP reports
attached to monthly payments certificate
4.1 All employees and EPWP participants contracts
4.2 All employees and EPWP participants certified SA
ID copies
4.3 All employees and EPWP attendance register
4.4 All employees and EPWP proof of payment
4.5 EPWP reports populated on standard templates
5. Penalties for non compliance
Acknowledge non compliance of R3000-00 (Three
thousand rand) per month per participant
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E15 | HIV/AIDS AWARENESS
It is required of the contractor to thoroughly study the
HIV/AIDS Specification (PW 1544) of the Department
that must be read together with and is deemed to be
incorporated under this Section of the Bills of Quantities.
Provision for pricing of HIV/AIDS awareness is made
under items E14.1 to E14.5 hereafter and it is explicitly
pointed out that all requirements of the aforementioned
specification are deemed to be priced hereunder, as the
said items represent the only method of measurement
and no additional items or extras to the contract in this
regard shall be entertained
The contractor must take note that compliance with the
HIV/AIDS Specification is compulsory. In the event of
partial or total non-compliance, the principal agent,
notwithstanding the provisions of Clause A 31.0 of
Section A or any other clause to the contrary, reserves
the right to delay issuing any progress payment
certificate until the contractor provides satisfactory
proof of compliance. The contractor shall not be
entitled to any compensation of whatsoever nature,
including interest, due to such delay of payment
E15.1 | AWARENESS CHAMPION
Selection, appointment, briefing and making available of
an Awareness Champion including provision of all
relevant services, all in accordance with the HIV/AIDS
Specification
| F: …………... V: ………….. T: …………… | Item | 1
E15.2 | AWARENESS WORKSHOPS
Selection and appointment of a competent Service
Provider approved by the principal agent, provision of
a Service Provider Workshop Plan and a suitable
venue, conducting of awareness workshops by means
of traditional and/or modern multimedia techniques,
including follow-up courses, making available all tuition
material and performing assessment procedures, all in
accordance with the HIV/AIDS Specification
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BROUGHT FORWARD
E15.3 | POSTERS, BOOKLETS, VIDEOS, ETC.
Provision, displaying, maintaining and replacing when
necessary of four plastic laminated posters, booklets
and educational videos, etc. for the duration of the
construction period, all in accordance with the
HIV/AIDS Specification
| F: …………... V: ………….. T: …………… | Item | 1
E15.4 | ACCESS TO CONDOMS
Provision and maintenance of condom dispensers fixed
in position, including male and female condoms,
replenishing male and female condoms on a daily basis
as required for the duration of the construction period,
all in accordance with the HIV/AIDS Specification
| F: …………... V: ………….. T: …………… | Item | 1
E15.5 | MONITORING
Monitoring HIV/AIDS awareness of workers, providing
the principal agent with access to information including
making available all reports, thoroughly completed and
reflecting the correct information, for the duration of the
construction period and close out, all in accordance
with the HIV/AIDS Specification
| F: …………... V: ………….. T: …………… | Item | 1
E16 | CONSTRUCTION VEHICLES FOR DELIVERY OF
EQUIPMENT
Allow for vehicles such as truck cranes, forklifts, etc for
the moving of the generator into place and delivery of
other necessary equipment for the project.
| F: …………... V: ………….. T: …………… | Item | 1
E17 | ALTERNATE POWER SUPPLIES FOR
CONSTRUCTION
Allow for the supply of portable generators and/or other
alternate power supplies for construction equipment in
the event of power failure on the premesis.
| F: …………... V: ………….. T: …………… | Item | 1
CARRIED FORWARD TO SECTION 6 SUMMARY

## Section 2
MARION ISLAND GENERATOR UPGRADE AND ELECTRICAL INSTALLATION
ELECTRICAL ENGINEERING SERVICES
TENDER NUMBER:
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
1.1 | EMERGENCY STANDBY GENERATOR ENGINE
Supply, Deliver, install and commissioning of prime standby generator complete as specified for the following sizes:
The Engine shall be a Diesel Fuelled, old starting liquid cooled, compression ignition, direct injection industrial type as complying with SANS 8528. The cooling system shall be thermostatically controlled entirely self-contained and shall consist of a radiator, fan and Circulation pump as per DPWI 722 specification.
The following from part of genset: Water jacket heater, fuel level indicator, fire fuse link shut off system,drip tray, battery charger, battery charger amp meter, canopy lights, fuel filling pump, Anti vibration mounts.
1.1.1 | 250kVA, 3 Phase Indoor Open Type Prime Genenator set | ea | 5
1.2 | 316 S/S CHANGE OVER PANEL WITH CONTROLLER
1.2.1 | The control shall contain the engine, alternator management and protection system, as well as the control logistics for the remote changeover switchgear. These functions shall be controlled by a micro-processor-based programmable control and it shall be equipped with an optional GSM cellphone-type modem as per DPWI 722 specifications (modem with sim card), c/w adjustable CB, motorized c/p & by pass switch
| Supply | ea | 5
LUBRICATION, OIL AND DIESEL
| Supply and fill up to 100% all required lubrications to run generator inclusing diesel. Tank shall be a 1300L capacity each | ea | 5
1.3 | EXHAUST SILENCER - Sound Attenuated
1.3.1 | Design supply and install the stainless steel exhaust silencer for the mentioned generator, including lagging: | ea | 5
1.5 | WARNING NOTICES
1.5.1 | Supply and Install warning notices on the container as specified.
| Set of Warning Notices as per SANS and OHS specifications. | ea | 5
1.6 | DOCUMENTATION
1.6.1 | Compilation of Maintenance, operational and technical
Manuals to the client satisfaction.
| Supply manuals | sum | 1
1.7 | SITE TESTING, COMMISSIONING & DOCUMENTATION
1.7.1 | Test and Commission to deliver a fully operational
generating set to the client and engineers satisfaction:
At the suppliers premises, prior to delivery to site
| On site after completion of the installation | ea | 5
1.8 | 1 YEAR MAINTENANCE
1.8.1 | 12 Month maintenance as per the specification.
| Quarterly (4) service of the plant as per the manufacturer’s requirements | Item | 20
CARRIED FORWARD
BROUGHT FORWARD
1.9 | PADLOCKS
1.9.1 | Supply and install A82 padlocks. | ea | 10
1.1 | DECOMMISSION
1.10.1 | Decommissioning of the existing generator sets and delivering to storage/appointed location. | ea | 5
CARRIED FORWARD TO SECTION 6 SUMMARY

## Section 3
MARION ISLAND GENERATOR UPGRADE AND ELECTRICAL INSTALLATION
ELECTRICAL ENGINEERING SERVICES
TENDER NUMBER:
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
3 | LT DISTRIBUTION AND SERVICE RETICULATION
3.1 | LOW VOLTAGE SUPPLY CABLES
Supply and install the following 600/1000V PVC/SWA/PVC cables with copper conductor to SABS 1507 laid vertically or horizontally in conduiting /ducting/clipped direct in accordance with the specifications and drawings, including fixing. (Termination elsewhere).
Generator Room (Technical Centre)
3.1.1 | 70mm² 4 core Gen 1 to Main Sync Control Panel | m | 60
3.1.2 | 70mm² 4 core Gen 2 to Main Sync Control Panel | m | 60
3.1.3 | 70mm² 4 core Gen 3 to Main Sync Control Panel | m | 60
3.1.4 | 95mm² 4 core Main Sync Control Panel to Main DB | m | 100
3.1.5 | 95mm² 4 core Main Sync Control Panel to Sync Control Panel (ADE Shack Room) | m | 500
ADE Shack Room
3.1.6 | 70mm² 4 core Gen 4 to Sync Control Panel | m | 60
3.1.7 | 70mm² 4 core Gen 5 to Sync Control Panel | m | 60
3.2 | CABLE TERMINATIONS
Termination of LV cables as specified including connection of conductors, cable lugs, captive glands, shrounds, etc. for the following cable sizes.
Generator Room (Technical Centre)
3.2.1 | 70mm² 4 core Gen 1 to Main Sync Control Panel | No | 4
3.2.2 | 70mm² 4 core Gen 2 to Main Sync Control Panel | No | 4
3.2.3 | 70mm² 4 core Gen 3 to Main Sync Control Panel | No | 4
3.2.4 | 95mm² 4 core Main Sync Control Panel to Main DB | No | 4
3.2.5 | 95mm² 4 core Main Sync Control Panel to Sync Control Panel (ADE Shack Room) | No | 4
ADE Shack Room
3.2.6 | 70mm² 4 core Gen 4 to Sync Control Panel | No | 4
3.2.7 | 70mm² 4 core Gen 5 to Sync Control Panel | No | 4
CARRIED FORWARD
BROUGHT FORWARD
3.3 | BARE COPPER EARTH WIRES
Supply and install 600/1000V conductors and bare stranded copper conductors on wire ways or trenching including terminations for earthing in accordance with the specifications and drawings
Generator Room (Technical Centre)
3.3.1 | 70mm² BCEW Gen 1 to Main Sync Control Panel | m | 30
3.3.2 | 70mm² BCEW Gen 2 to Main Sync Control Panel | m | 30
3.3.3 | 70mm² BCEW Gen 3 to Main Sync Control Panel | m | 30
3.3.4 | 95mm² BCEW Main Sync Control Panel to Main DB | m | 50
3.3.5 | 95mm² BCEW Main Sync Control Panel to Sync Control Panel (ADE Shack Room) | m | 250
ADE Shack Room
3.3.6 | 70mm² BCEW Gen 4 to Sync Control Panel | m | 30
3.3.7 | 70mm² BCEW Gen 5 to Sync Control Panel | m | 30
3.4 | BARE COPPER EARTH WIRES TERMINATIONS
Termination of BCEW cables as specified including connection of conductors, cable lugs, captive glands, shrounds, etc. for the following cable sizes.
Generator Room (Technical Centre)
3.4.1 | 70mm² BCEW Gen 1 to Main Sync Control Panel | No | 2
3.4.2 | 70mm² BCEW Gen 2 to Main Sync Control Panel | No | 2
3.4.3 | 70mm² BCEW Gen 3 to Main Sync Control Panel | No | 2
3.4.4 | 95mm² BCEW Main Sync Control Panel to Main DB | No | 2
3.4.5 | 95mm² BCEW Main Sync Control Panel to Sync Control Panel (ADE Shack Room) | No | 2
ADE Shack Room
3.4.6 | 70mm² BCEW Gen 4 to Sync Control Panel | No | 2
3.4.7 | 70mm² BCEW Gen 5 to Sync Control Panel | No | 2
CARRIED FORWARD
BROUGHT FORWARD
3.5 | CABLE BUSKET
Supply and Install Heavy duty galvanised Cable ladder including all supports etc.
3.5.1 | 300mm wide | sum | 1
3.6 | JOINTING KIT
3.6.1 | Jointing of LV cables as specified with all the accessories | sum | 1
3.7 | GENERAL
3.7.1 | Test, commission, and certify complete LT reticulation and distribution in accordance with the specifications | sum | 1
3.8 | EARTHING AND ACCESSORIES
Supply and install 1.2 m long copper coated earth spike incl earth clamp and earth coupling on Distribution Board
3.8.1 | 1.2m earth spike | No | 14
3.9 | DISTRIBUTION BOARDS
Supply of distribution boards including delivery to site
Installation of boards including moving into position, connecting up to all trunking and conduit, circuit and earthing terminations and compilation of legend cards but excluding cable terminations which are measured elsewhere.
3.9.1 | Main Distribution Board | ea | 1
Physical size parameters
1100 mm Wide, 1800 mm High, 400 mm Deep
Circuit breakers to be cascaded as per drawing MI_DEFF_E_SLD_004
Allow for additional 350 Amp 3P circuit breaker fed from Main Sync Control Panel. 350 Amp Circuit breaker to be connected to BUSBAR system, and feeding out to distribution circuit breakers, cascaded as per drawing MI_DEFF_E_SLD_004
CARRIED FORWARD
BROUGHT FORWARD
3.9.2 | Synchronization Distribution and Generator Control Panel (Main Sync Control Panel) | ea | 1
Physical size parameters
3200 mm Wide, 1830 mm High, 800 mm Deep
Cables bottom entry, floor standing Red finish indoor DB with doors Panel to be 316 S/S
3.9.2.1 | Section No 1 - Alternator Set 1
350 Amp Motorized circuit breaker to be fed from 250kVA generator according to monitor Generator specifications
350 Amp circuit breakers to be connected to a BUSBAR system and feeding out to a 350 Amp circuit breaker to feed Main Distribution DB
Panel to include Hub for the SCADA connections from generator controllers to 8610 MIMIC Panel
Deep Sea or approved battery charger
Front Panel lock-out key switch for maintenance lock-out
All relevant controls such as Oil, Temp etc as per 8610 wiring diagram
Front panel plug point to work only if generator operation incl. contrl gear and protection
Control gear to alternator heater and Engine water heater
Emergency stop
CARRIED FORWARD
BROUGHT FORWARD
3.9.2.2 | Section No 2 - Alternator Set 2
350 Amp Motorized circuit breaker to be fed from 250kVA generator according to monitor Generator specifications
350 Amp circuit breakers to be connected to a BUSBAR system and feeding out to a 350 Amp circuit breaker to feed Main Distribution DB
Panel to include Hub for the SCADA connections from generator controllers to 8610 MIMIC Panel
Deep Sea or approved battery charger
Front Panel lock-out key switch for maintenance lock-out
All relevant controls such as Oil, Temp etc as per 8610 wiring diagram
Front panel plug point to work only if generator operation incl. contrl gear and protection
Control gear to alternator heater and Engine water heater
Emergency stop
3.9.2.3 | Section No 3 - Alternator Set 3
350 Amp Motorized circuit breaker to be fed from 250kVA generator according to monitor Generator specifications
350 Amp circuit breakers to be connected to a BUSBAR system and feeding out to a 350 Amp circuit breaker to feed Main Distribution DB
Panel to include Hub for the SCADA connections from generator controllers to 8610 MIMIC Panel
Deep Sea or approved battery charger
Front Panel lock-out key switch for maintenance lock-out
All relevant controls such as Oil, Temp etc as per 8610 wiring diagram
CARRIED FORWARD
BROUGHT FORWARD
Front panel plug point to work only if generator operation incl. contrl gear and protection
Control gear to alternator heater and Engine water heater
Emergency stop
3.9.2.4 | Section No 4 - ADE SHACK MAIN BUS
350 Amp Motorized circuit breaker to be fed from Sync Control Panel (ADE Shack Room) according to monitor Generator specifications and as per drawing MI_DAFF_E_CP_001
350 Amp circuit breakers to be connected to a BUSBAR system and feeding out to a 350 Amp circuit breaker to feed Main Distribution DB
3.9.2.5 | Section No 5 - INCOMER MAIN BREAKER
350 Amp Motorized circuit breaker to be fed from the Main Sync Control Panel BUSBAR according to monitor Generator specifications and as per drawing MI_DAFF_E_CP_001
350 Amp circuit breakers to be connected to a BUSBAR system and feeding out to a 350 Amp circuit breaker to feed Main Distribution DB
3.9.2.6 | Section No 6
Generator No1 controls with Deep Sea 8610 Controller or approved, Sync ready.
Generator No2 controls with Deep Sea 8610 Controller or approved, Sync ready.
Generator No3 controls with Deep Sea 8610 Controller or approved, Sync ready.
Multi-set remote overview display Deep Sea 8003 contoller, or approved, Sync ready.
Controller 1 with DSE124 CANBUS Extender Controller or approved, Sync ready.
Deep Sea or approved battery charger
Contols etc as per Section No 1
CARRIED FORWARD
BROUGHT FORWARD
3.9.3 | ADE Shack Generator Control DB (Sync Control Panel (ADE Shack Room)) | ea | 1
Physical size parameters
1800 mm Wide, 1830 mm High, 400 mm Deep
Cables bottom entry, floor standing Red finish indoor DB with doors Panel to be 316 S/S
3.9.3.1 | Section No 1
350 Amp Motorized circuit breaker to be fed from 250kVA generator according to monitor Generator specifications
350 Amp circuit breakers to be connected to a BUSBAR system and feeding out to a 350 Amp circuit breaker to feed Main Sync Control Panel
Panel to include Hub for the SCADA connections from generator controllers to 8610 MIMIC Panel
Deep Sea or approved battery charger
Front Panel lock-out key switch for maintenance lock-out
All relevant controls such as Oil, Temp etc as per 8610 wiring diagram
Front panel plug point to work only if generator operation incl. contrl gear and protection
Control gear to alternator heater and Engine water heater
Emergency stop
3.9.3.2 | Section No 2
350 Amp Motorized circuit breaker to be fed from 250kVA generator according to monitor Generator specifications
350 Amp circuit breakers to be connected to a BUSBAR system and feeding out to a 350 Amp circuit breaker to feed Main Sync Control Panel
Panel to include Hub for the SCADA connections from generator controllers to 8610 MIMIC Panel
Deep Sea or approved battery charger
CARRIED FORWARD
BROUGHT FORWARD
Front Panel lock-out key switch for maintenance lock-out
All relevant controls such as oil, temp etc as per 8610 wiring diagram
Front panel plug point to work only if generator operation incl. contrl gear and protection
Control gear to alternator heater and Engine water heater
Emergency stop
3.9.3.3 | Section No 3 - INCOMER MAIN BREAKER
350 Amp Motorized circuit breaker to be fed from the Sync Control Panel (ADE Shack Room) according to monitor Generator specifications and as per drawing MI_DAFF_E_CP_002
350 Amp circuit breakers to be connected to a BUSBAR system and feeding out to a 350 Amp circuit breaker to feed Main Sync Control Panel
3.9.3.4 | Section No 4
Generator No1 controls with Deep Sea 8610 Controller or approved, Sync ready.
Generator No1 controls with Deep Sea 8610 Controller or approved, Sync ready.
Controller 2 with DSE124 CANBUS Extender Controller or approved, Sync ready.
Deep Sea or approved battery charger
Contols etc as per Section No 1
3.9.4 | ADE Shack Main DB | ea | 1
Physical size parameters
1100 mm Wide, 1800 mm High, 400 mm Deep
Cables bottom entry, Floor Standing Red Finish Indoor DB with doors 316 S/S
Circuit breakers to be cascaded as per drawing MI_DEFF_E_SLD_005
CARRIED FORWARD
BROUGHT FORWARD
3.9.5 | Test and Issue Certificates of Compliance in accordance with SANS 10142 and the Occupational Health and Safety Act. | sum | 1
Main Distribution Board
Synchronization Distribution and Geneator Control Panel (Main Sync Control Panel)
ADE Shack Generator Control Panel (Sync Control Panel (ADE Shack Room))
ADE Shack Main DB
3.9.6 | General
| Test, commission and certify complete L.T reticulation and distribution in accordance with the specifications | sum | 1
CARRIED FORWARD TO SECTION 6 SUMMARY

## Section 4
MARION ISLAND GENERATOR UPGRADE AND ELECTRICAL INSTALLATION
ELECTRICAL ENGINEERING SERVICES
TENDER NUMBER:
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
4 | ELECTRICAL INSTALLATION
4.1 | Trunking
Supply and Install galvanized trunking suspended on hangers 600mm below slab soffit or roof structure inclusive of splices; hanging brackets; fixings, steel covers, bends etc.
4.1.1 | P8000 | m | 20
4.1.2 | P2000 | m | 20
4.2 | Conduit and Boxes
Galvanized conduit inclusive fixings, fittings, adaptors and locknut etc.
4.2.1 | 20mm diameter | m | 50
PVC boxes installed including Galvanised conduit ends
4.2.2 | 100x50x50mm surface box | ea | 4
4.2.3 | 100x100x50mm surface box | ea | 50
4.3 | Conductors
PVC insulated black 'UV resistant' surfix cable with aluminium sheath and copper conductors
4.3.1 | 2,5mm²/2c | m | 100
PVC insulated black 'UV resistant' surfix terminators
4.3.2 | 2,5mm²/2c terminations | ea | 10
4.4 | Socket Outlets
Supply and Install Crabtree Classic, similar or proven equivalent, outlets including cradies and covers including wire terminations
4.4.1 | 16A duo normal switched socket outlets | ea | 10
Allow for the supply, acceptance, storage, fixing and connecting up of the following luminaires excluding cutting of holes including wire terminations for surface mounted fittings
4.4.2 | Vapour Proof Luminaire 5ft | ea | 10
4.5 | Light Switches
Supply and Install Crabtree Classic , similar or proven equivalent, light switches including conductor terminations
4.5.1 | 1 lever 1 way | ea | 4
4.6 | General
| Test and commission complete general power and lighting installation | sum | 1
4.6.1 | Supply as-built documentation | sum | 1
CARRIED FORWARD TO SECTION 6 SUMMARY

## Section 5
MARION ISLAND GENERATOR UPGRADE AND ELECTRICAL INSTALLATION
ELECTRICAL ENGINEERING SERVICES
TENDER NUMBER:
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
5 | PRIME COST SUMS
5.1 | Distribution Boards
Sum for the supply of distribution boards including delivery to site
5.1.1 | Main Distribution Board | ea | 1
5.1.2 | Synchronization Distribution and Generator Control Panel | ea | 1
5.1.3 | ADE Shack Generator Control DB | ea | 1
5.1.4 | ADE Shack Main DB | ea | 1
5.2 | Luminaires
Sum for the supply only to site of the following luminaires;
5.2.1 | Vapour Loom | ea | 10
CARRIED FORWARD TO SECTION 6 SUMMARY

## Section 6
MARION ISLAND GENERATOR UPGRADE AND ELECTRICAL INSTALLATION
ELECTRICAL ENGINEERING SERVICES
TENDER NUMBER:
SECTION 6 : FINAL SUMMARY
SECTION |  | AMOUNT
1 | PRELIMINARIES AND GENERAL
2 | GENERATOR INSTALLATION
3 | LT DISTRIBUTION AND SERVICE RETICULATION
4 | ELECTRICAL INSTALATION
5 | PRIME COST SUMS |  | 0
25mm2 x 4 core
10mm2 PVC Insulated Earth Wire
0
TOTAL TENDERED VALUE EXCLUDING. VAT.
15% VAT
TOTAL TENDERED VALUE INCLUDING VAT. CARRIED TO FORM OF OFFER AND ACCEPTANCE DPW-07(EC)

## Sheet1 (hidden)
MAKHADO SAPS GENERATOR INSTALLATION
ELECTRICAL ENGINEERING SERVICES
TENDER NO.: . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .
| DESCRIPTION |  | AMOUNT
| PRELIMINARIES AND GENERALS………………………. |  | 0
| ENGINE SET INSTALLATION . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 0
| ELECTRICAL AND CABLES. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 0
| TESTING, COMMISSIONING AND DOCUMENTATION. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 0
| 1 YEAR MAINTENANCE PLAN. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 0
| STRUCTURAL - TYPICAL GENERATOR BASE. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | #REF!
| TOTAL (Excl. VAT)………………………………………….……………. |  | #REF!
| 15% VAT |  | #REF!
| TOTAL TENDERED VALUE INCLUDING VAT. CARRIED TO FORM AND OFFER |  | #REF!
AND ACCEPTANCE DPW-07(EC)